## Single Duct Quick Select
VariTrane™ Single Duct VAV Quick Select
This tool is designed for estimating and scoping . For complete selection performance the Trane® Select AssistTM should be used.
Instructions:
1. Select Inlet Size
2. Check appropriate factors. Re-select inlet size as needed.
Inlet Size
Airflow and Acoustics
Airflow (CFM)1 |  | Unit Radiated NC2 |  | Unit Discharge NC2
Max | Min | 50% Max Flow | 80% Max Flow | 50% Max Flow | 80% Max Flow
------ | ------ | ------ | ------ | ------ | ------
Unit Dimensions
(Length x Width x Height, Inches)3
| VCCF | VCEF | VCWF
| ------ | ------ | ------
Unit Air Pressure Drop
Airflow (CFM) | APD (in. w.g) |  | Airflow (CFM) | APD (in. w.g)
| VCCF | VCEF |  | VCCF | VCEF
------ | ------ | ------ | ------ | ------ | ------
Electric Reheat (VCEF)
Airflow (CFM) | Max Capacity (kW)4 | Air Temp Rise (°F) | Airflow (CFM) | Max Capacity (kW)4 | Air Temp Rise (°F)
------ | ------ | ------ | ------ | ------ | ------
Unit LAT reccommended to be 20°F higher than space setpoint to ensure proper mixing
Hot Water Reheat (VCWF)
1-Row Coil
Fluid Flow (GPM) |  |  | Fluid Pressure Drop (ft. H2O)
------ |  |  | ------
Airflow (CFM) | Capacity (MBH)5 | APD (in. w.g.) | Airflow (CFM) | Capacity (MBH)5 | APD (in. w.g.)6
------ | ------ | ------ | ------ | ------ | ------
2-Row Coil
Fluid Flow (GPM) |  |  | Fluid Pressure Drop (ft. H2O)
------ |  |  | ------
Airflow (CFM) | Capacity (MBH)5 | APD (in. w.g.) | Airflow (CFM) | Capacity (MBH)5 | APD (in. w.g.)6
------ | ------ | ------ | ------ | ------ | ------
3-Row Coil
Fluid Flow (GPM) |  |  | Fluid Pressure Drop (ft. H2O)
------ |  |  | ------
Airflow (CFM) | Capacity (MBH)5 | APD (in. w.g.) | Airflow (CFM) | Capacity (MBH)5 | APD (in. w.g.)6
------ | ------ | ------ | ------ | ------ | ------
4-Row Coil
Fluid Flow (GPM) |  |  | Fluid Pressure Drop (ft. H2O)
------ |  |  | ------
Airflow (CFM) | Capacity (MBH)5 | APD (in. w.g.) | Airflow (CFM) | Capacity (MBH)5 | APD (in. w.g.)6
------ | ------ | ------ | ------ | ------ | ------
VCWF Example: 8 in. Inlet Size, 1-Row Coil, has a fluid flow rate range of 0.6-2.5 and a fluid pressure drop range of 1.0-12.1. At fluid flow rate of 0.6 GPM and airflow of 350 CFM, the capacity is 13.8 MBH and the APD is 0.14 in. w.g.
Notes
1. Minimum airflows shown are to maintain pressure independence. Absolute minimums are 0 cfm.
2. NC values shown are based on VCCF with 0.75 in. w.g. inlet static pressure, 0.25 in. w.g downstream static pressure and AHRI
885-08 transfer functions. NC values for VCCF model. Ultiize Trane® Select AssistTM for additional acoustical performance.
3. VCCF and VCWF width includes 5.5 in. for control enclosure VCEF width includes 6 in. for controls enclosure Length includes inlet reducer (sizes 4 & 5), inlet cylinder and discharge slip & drive connection VCWF length includes 1/2-row coil length. Add 1.5 in. for 3 and 4-row coils
4. Max kW available depends on voltage and stages required
5. Capacity based on 55°F entering air temperature and 180°F entering water temperature
6. Air pressure drop includes unit and hot water coil
Calculations
Air ΔT = (kW * 3145)/Airflow
MBH = 500*(H2O ΔT)*GPM = 1.085*(Air ΔT)*CFM
MBH = 1.085*(Air ΔT)*CFM
Definitions and Units
VCCF = Single duct VAV unit without reheat
VCEF = Single duct VAV unit with electric reheat
VCWF = Single duct VAV unit with hot water reheat
NC = Noise Criteria |  |  |  |  | 2020-11-17
APD = Air pressure drop [in. w.g] |  |  |  |  | Rev 2

## Fan Powered Quick Select
VariTrane™ Fan Powered VAV Quick Select
This tool is designed for estimating and scoping . For complete selection performance the Trane® Select AssistTM should be used.
Instructions:
1. Select Configuration Type, Fan Size and Motor Type
2. Check appropriate factors. Re-select Configuration Type, Fan Size and Motor Type as needed.
02/07 ECM Check
Configuration Type |  |  | Fan Size |  |  | Motor Type |  | 0
Fan Airflow (CFM) Range @ 0.25 in. wg. Downstream SP |  |  | ------ |  | Inlet Size Availability (Ø inches) |  | ------ | User Input
Unit Configuration
Parallel
Acoustics NC Value1 | [7 empty] | Series
|  | No Attenuator |  |  | With Suppressor Attenuator
Sound Path |  | Minimum Airflow | 50% Airflow | Maximum Airflow | Minimum Airflow | 50% Airflow | Maximum Airflow
Radiated Fan |  | ------ | ------ | ------ | ------ | ------ | ------ | Fan Size
Discharge Fan |  | ------ | ------ | ------ | ------ | ------ | ------ | 02SQ
------ |  | ------ | ------ | ------ | ------ | ------ | ------ | 03SQ
------ |  | ------ | ------ | ------ | ------ | ------ | ------ | 04SQ
05SQ
Dimensions | [7 empty] | 06SQ
Unit Model | ------ |  | ------ |  | ------ |  |  | 07SQ
L x W x H (inches)2 | ------ |  | ------ |  | ------
Electric Heat Capacity Range (kW)3 |  | ------ | [5 empty] | Motor Type | Radiated Fan | Radiated Fan
[8 empty] | PSC | Discharge Fan | Discharge Fan
Hot Water Heat | [7 empty] | ECM | Radiated Valve | Radiated Valve&Fan
| 1-Row | 2-Row | [6 empty] | Discharge Valve
Maximum Airflow (CFM)4 | ------ | ------
1-Row Coil Performance
Fluid Flow (GPM) | Fluid Pressure Drop (ft. H2O) | Airflow (CFM) | Capacity (MBH) | APD (in. wg.) | Airflow (CFM) | Capacity (MBH) | APD (in. wg.)
------ | ------ | ------ | ------ | ------ | ------ | ------ | ------
2-Row Coil Performance
Fluid Flow (GPM) | Fluid Pressure Drop (ft. H2O) | Airflow (CFM) | Capacity (MBH) | APD (in. wg.) | Airflow (CFM) | Capacity (MBH) | APD (in. wg.)
------ | ------ | ------ | ------ | ------ | ------ | ------ | ------
Example: Series configuration (VSWF), 04SQ fan size, ECM motor type, 1-Row Coil, has a maximum airflow of 1,495, fluid flow rate range of 0.5-8 GPM and a fluid pressure drop range of 0.07-13.44 ft. H2O. At fluid flow rate of 0.5 GPM and airflow of 1121 CFM, the capacity is 15.59 MBH and the APD is 0.096 in. w.g.
Notes
1. NC values shown are based on VCCF with 0.75 in. w.g. inlet static pressure, 0.25 in. w.g downstream static pressure and AHRI 885-08 transfer functions. NC values for VPCF and VSCF models. Ultiize Trane® Select AssistTM for additional acoustical performance.
2. Width includes 5.5 in. for control enclosure Length does NOT include inlet cylinder (4 in. for inlet sizes 6-16 in. and 6.5 in. for inlet size 5 in.) Series configuration narrow corridor option adds 6.4 in. to width Suppressor attenuator adds 16 in. to length for parallel configuration Suppressor attenuator adds (02SQ 14 in., 03SQ-05SQ 16 in., 06SQ-07SQ 20 in.) to width for series config.
3. Max kW available depends on voltage and stages required
4. Maximum airflow based on 0.25 in. wg. downstream static pressure
5. Coil located on plenum inlet for parallel configuration (unit discharge optional ) Coil location on unit discharge for series configuration Capacity based on 55°F entering primary air, 70°F entering plenum air and 180°F entering water Entering air conditions 62.5°F for series configuration (50% primary air and 50% plenum air)
Calculations
Air ΔT = (kW * 3145)/Airflow
MBH = 500*(H2O ΔT)*GPM = 1.085*(Air ΔT)*CFM
MBH = 1.085*(Air ΔT)*CFM
Definitions and Units
VPCF = Parallel FP VAV unit without reheat
VPEF = Parallel FP VAV unit with electric reheat
VPWF = Parallel FP VAV unit with hot water reheat
VSCF = Series FP VAV unit without reheat
VSEF = Series FP VAV unit with electric reheat
VSWF = Series FP VAV unit with hot water reheat
NC = Noise Criteria | [6 empty] | 2020-11-17
APD = Air pressure drop [in. w.g] | [6 empty] | Original

## FP Background Data (hidden)
Hot Water Reheat
|  | Parallel | Series | Parallel | Series | Dimensions (L x W x H inches) | [5 empty] | Electric Reheat |  | Hot Water Reheat Max Airflow (cfm) |  |  |  | Parallel | [15 empty] | Series
|  | Fan Airflow Range (cfm) @ 0.25" wg. Downstream SP | Fan Airflow Range (cfm) @ 0.25" wg. Downstream SP | Inlet Size Availability (Ø in.) | Inlet Size Availability (Ø in.) | Parallel |  |  | Series |  |  | kW Available |  | Parallel |  | Series |  | 1 Row Coil | [7 empty] | 2 Row Coil | [7 empty] | 1 Row Coil | [7 empty] | 2 Row Coil
Fan Size | Motor Type |  |  |  |  | VPCF | VPWF | VPEF | VSCF | VSWF | VSEF | Parallel | Series | 1 row | 2 row | 1 row | 2 row | GPM | ΔP | CFM | MBH | APD | CFM | MBH | APD | GPM | ΔP | CFM | MBH | APD | CFM | MBH | APD | GPM | ΔP | CFM | MBH | APD | CFM | MBH | APD | GPM | ΔP | CFM | MBH | APD | CFM | MBH | APD
02SQ | PSC | 122-455 | 190-695 | 5, 6, 8, 10 | 4, 5, 6, 8, 10 | 30x45.5x15.5 | 36.3x45.5x15.5 | 36x45.5x15.5 | 34x27.5x15.5 | 40.75x27.5x15.5 | 52.5x27.5x15.5 | 0.5-6.0 | 0.5-7.0 | 445 | 425 | 645 | 600 | 0.5-5 | 0.21-13.02 | 333.75 | 13.09-20.43 | 0.012 | 445 | 14.23-23.58 | 0.019 | 1-1 | 1.21-1.21 | 318.75 | 23.1-23.1 | 0.023 | 425 | 26.87-26.87 | 0.037 | 0.5-5 | 0.15-9.01 | 483.75 | 12.4-20.69 | 0.055 | 645 | 13.43-24.05 | 0.091 | 1-5 | 0.93-16.25 | 450 | 25.09-33.15 | 0.095 | 600 | 28.01-39.25 | 0.153
03SQ | PSC | 252-1095 | 254-1185 | 6, 8, 10, 12 | 6, 8, 10, 12 | 32.5x45.5x17.5 | 38.8x45.5x17.5 | 38.5x45.5x17.5 | 40x29.5x17.5 | 50.75x29.5x17.5 | 58.5x29.5x17.5 | 0.5-11.0 | 0.5-14.0 | 1050 | 1010 | 1150 | 1110 | 0.5-10 | 0.07-20.9 | 787.5 | 14.21-35.91 | 0.045 | 1050 | 14.87-41.78 | 0.074 | 1-10 | 0.33-24.91 | 757.5 | 33.44-57.49 | 0.084 | 1010 | 36.03-68.85 | 0.133 | 0.5-8 | 0.07-13.44 | 862.5 | 14.99-38.64 | 0.06 | 1150 | 15.64-44.88 | 0.1 | 1-8 | 0.37-17.62 | 832.5 | 35.95-63.08 | 0.112 | 1110 | 38.48-74.59 | 0.18
04SQ | PSC | 300-1325 | 330-1555 | 8, 10, 12, 14 | 6, 8, 10, 12, 14 | 32.5x45.5x17.5 | 38.8x45.5x17.5 | 38.5x45.5x17.5 | 40x29.5x17.5 | 5075x29.5x17.5 | 58.5x29.5x17.5 | 0.5-14.0 | 0.5-18.0 | 1255 | 1185 | 1490 | 1425 | 0.5-10 | 0.07-20.9 | 941.25 | 14.62-39.42 | 0.061 | 1255 | 15.25-45.95 | 0.102 | 1-10 | 0.33-24.92 | 888.75 | 34.94-63.68 | 0.108 | 1185 | 37.29-75.54 | 0.174 | 0.5-8 | 0.07-13.44 | 1117.5 | 15.58-44.22 | 0.095 | 1490 | 16.2-51.41 | 0.16 | 1-8 | 0.37-17.63 | 1068.75 | 38.17-73.04 | 0.169 | 1425 | 40.33-85.04 | 0.275
05SQ | PSC | 350-1540 | 405-1900 | 10, 12, 14 | 10, 12, 14 | 32.5x45.5x17.5 | 38.8x45.5x17.5 | 38.5x45.5x17.5 | 40x35.5x17.5 | 50.75x35.5x17.5 | 58.5x35.5x17.5 | 0.5-18.0 | 0.5-22.0 | 1405 | 1310 | 1740 | 1640 | 0.5-10 | 0.07-20.9 | 1053.75 | 14.87-41.86 | 0.075 | 1405 | 15.48-48.81 | 0.125 | 1-10 | 0.33-24.92 | 982.5 | 35.81-67.73 | 0.127 | 1310 | 38.01-79.84 | 0.205 | 0.5-8 | 0.08-14.11 | 1305 | 17.32-52.94 | 0.11 | 1740 | 17.91-61.41 | 0.186 | 1-8 | 0.37-17.37 | 1230 | 42.27-86.12 | 0.187 | 1640 | 44.36-100.46 | 0.306
06SQ | PSC | 880-1875 | 700-2625 | 10, 12, 14, 16 | 10, 12, 14, 16 | 40x45.5x21.5 | 46.3x45.5x21.5 | 46x45.5x21.5 | 40x35.5x21.5 | 46.75x35.5x21.5 | 57x35.5x21.5 | 0.5-20.0 | 0.5-22.0 | 1710 | 1600 | 2470 | 2335 | 0.5-7 | 0.1-11.03 | 1282.5 | 18.35-47.83 | 0.066 | 1710 | 19.1-55.38 | 0.11 | 1-7 | 0.62-18.9 | 1200 | 40.95-77.24 | 0.114 | 1600 | 43.18-90.07 | 0.184 | 0.5-6 | 0.11-9.16 | 1852.5 | 21.35-64.92 | 0.11 | 2470 | 22.01-74.87 | 0.186 | 1.5-6 | 1.46-16.74 | 1751.25 | 63.82-105.12 | 0.187 | 2335 | 67.47-119.57 | 0.303
07SQ | PSC | 1000-2020 | 850-3015 | 10, 12, 14, 16 | 10, 12, 14, 16 | 40x45.5x21.5 | 46.3x45.5x21.5 | 46x45.5x21.5 | 40x35.5x21.5 | 46.75x35.5x21.5 | 57x35.5x21.5 | 0.5-20.0 | 0.5-24.0 | 1800 | 1660 | 2675 | 2445 | 0.5-7.5 | 0.1-12.52 | 1350 | 18.49-49.45 | 0.072 | 1800 | 19.23-57.35 | 0.121 | 1-7.5 | 0.62-21.39 | 1245 | 41.27-79.5 | 0.121 | 1660 | 43.43-92.65 | 0.195 | 0.5-6 | 0.11-9.17 | 2006.25 | 21.54-67.54 | 0.127 | 2675 | 22.18-77.86 | 0.215 | 1.5-6 | 1.46-16.74 | 1833.75 | 64.45-107.45 | 0.202 | 2445 | 67.99-121.85 | 0.328
03SQ | ECM | 168-1075 | 201-1095 | 6, 8, 10, 12 | 6, 8, 10, 12 | 32.5x45.5x17.5 | 38.8x45.5x17.5 | 38.5x45.5x17.5 | 40x29.5x17.5 | 50.75x29.5x17.5 | 58.5x29.5x17.5 | 0.5-11.0 | 0.5-14.0 | 1055 | 1035 | 1095 | 1095 | 0.5-10 | 0.07-20.9 | 791.25 | 14.22-35.98 | 0.045 | 1055 | 14.88-41.89 | 0.075 | 1-10 | 0.33-24.91 | 776.25 | 33.67-58.38 | 0.087 | 1035 | 36.23-69.85 | 0.139 | 0.5-8 | 0.07-13.44 | 821.25 | 14.87-37.66 | 0.055 | 1095 | 15.54-43.75 | 0.092 | 1-8 | 0.37-17.62 | 821.25 | 35.82-62.53 | 0.11 | 1095 | 38.37-74.03 | 0.176
04SQ | ECM | 222-1500 | 263-1495 | 8, 10, 12, 14 | 6, 8, 10, 12, 14 | 32.5x45.5x17.5 | 38.8x45.5x17.5 | 38.5x45.5x17.5 | 40x29.5x17.5 | 5075x29.5x17.5 | 58.5x29.5x17.5 | 0.5-14.0 | 0.5-18.0 | 1450 | 1415 | 1495 | 1345 | 0.5-10 | 0.07-20.9 | 1087.5 | 14.94-42.58 | 0.079 | 1450 | 15.54-49.64 | 0.133 | 1-10 | 0.33-24.92 | 1061.25 | 36.43-70.88 | 0.144 | 1415 | 38.53-83.19 | 0.234 | 0.5-8 | 0.07-13.44 | 1121.25 | 15.59-44.29 | 0.096 | 1495 | 16.21-51.5 | 0.161 | 1-8 | 0.37-17.63 | 1008.75 | 37.69-70.68 | 0.154 | 1345 | 39.93-82.6 | 0.249
05SQ | ECM | 281-1835 | 350-2050 | 10, 12, 14 | 10, 12, 14 | 32.5x45.5x17.5 | 38.8x45.5x17.5 | 38.5x45.5x17.5 | 40x35.5x17.5 | 50.75x35.5x17.5 | 58.5x35.5x17.5 | 0.5-18.0 | 0.5-22.0 | 1660 | 1455 | 2035 | 1465 | 0.5-10 | 0.07-20.91 | 1245 | 15.23-45.75 | 0.101 | 1660 | 15.81-53.38 | 0.17 | 1-10 | 0.33-24.92 | 1091.25 | 36.66-72.05 | 0.151 | 1455 | 38.71-84.41 | 0.246 | 0.5-8 | 0.08-14.12 | 1526.25 | 17.64-57.39 | 0.146 | 2035 | 18.21-66.59 | 0.249 | 1.5-8 | 0.76-17.37 | 1098.75 | 52.53-80.67 | 0.156 | 1465 | 56.9-94.78 | 0.252
06SQ | ECM | 895-2075 | 700-2495 | 10, 12, 14, 16 | 10, 12, 14, 16 | 40x45.5x21.5 | 46.3x45.5x21.5 | 46x45.5x21.5 | 40x35.5x21.5 | 46.75x35.5x21.5 | 57x35.5x21.5 | 0.5-16.0 | 0.5-22.0 | 1950 | 1845 | 2480 | 2090 | 0.5-7 | 0.1-11.03 | 1462.5 | 18.7-51.14 | 0.083 | 1950 | 19.42-59.24 | 0.14 | 1-7 | 0.62-18.91 | 1383.75 | 42.12-83.55 | 0.144 | 1845 | 44.11-96.53 | 0.234 | 0.5-6 | 0.11-9.16 | 1860 | 21.36-65.05 | 0.111 | 2480 | 22.02-75.02 | 0.187 | 1.5-6 | 1.46-16.72 | 1567.5 | 62.21-99.54 | 0.156 | 2090 | 66.15-114.03 | 0.251
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50
[6 empty] | Width includes 5.5 in. for control enclosure | [8 empty] | Assuming 0.25 in. wg. downstream static pressure
User Input | [5 empty] | Length does NOT include inlet cylinder (4 in. for inlet sizes 6-16 in. and 6.5 in. for inlet size 5 in.) | [8 empty] | Hot water coil on inlet for parallel configuration |  |  | 1 Row Coil CFM: Use 75% maximum airflow; 1 Row Coil CFM: Use 100% maximum airflow; 1 Row Coil ΔP: Use 75% maximum airflow; 1 Row Coil CFM: Use 100% maximum airflow
Unit Configuration | [5 empty] | Series configuration narrow corridor option adds 6.4 in. to width | [8 empty] | Assuming 1 in. Throwaway return air filter |  |  | 1 Row Coil CFM: 70F EAT; 1 Row Coil CFM: 70F EAT; 1 Row Coil ΔP: 180F EWT; 1 Row Coil CFM: 180F EWT
Parallel | [5 empty] | Suppressor sound attenuator adds 16 in. to length for parallel | [11 empty] | 1 Row Coil CFM: 180F EWT; 1 Row Coil CFM: 180F EWT; 1 Row Coil ΔP: 55F Primary EAT; 1 Row Coil CFM: 55F Primary EAT
Series | [5 empty] | Suppressor sound attenuator adds (02SQ 14 in., 03SQ-05SQ 16 in., 06SQ-07SQ 20 in.) to width for series | [11 empty] | 1 Row Coil ΔP: 70F Plenum EAT; 1 Row Coil CFM: 70F Plenum EAT
[35 empty] | 62.5F coil EAT |  |  |  | 62.5F coil EAT
Fan Size
02SQ | [5 empty] | Should I add FLA?
03SQ
04SQ
05SQ
06SQ
07SQ
Motor Type
PSC
ECM
Radiated Fan
Discharge Fan
Radiated Valve
Discharge Valve
Radiated Valve&Fan
Discharge Fan
Radiated Valve

## VPWF Data (hidden)
VPWF - PSC Motor - 1R Coil | [11 empty] | 1+1 | 1+2 | 2+1 | 2+2 |  | VPWF - PSC Motor
Unit Tag | Fan size | Motor Type | Coil Rows | Airflow 1 | Airflow 2 | APD 1 | APD 2 | Fluid Flow 1 | Fluid Flow 2 | WPD 1 | WPD 2 | Capacity 1 | Capacity 2 | Capacity 3 | Capacity 4 |  | Unit Tag | Fan size | Motor Type | Airflow | Coil Rows | Fluid Flow | WPD | APD | Capacity | Fan TSP | Downstream SP
VPWF 02 1R PSC | 02SQ | PSC | 1 | 333.75 | 445 | 0.012 | 0.019 | 0.5 | 5 | 0.21 | 13.02 | 13.09 | 20.43 | 14.23 | 23.58 | - | VPWF 02 1R PSC | 02SQ | PSC | 333.75 | 1 | 0.5 | 0.21 | 0.012 | 13.09 | 0.262 | 0.25
VPWF 03 1R PSC | 03SQ | PSC | 1 | 787.5 | 1050 | 0.045 | 0.074 | 0.5 | 10 | 0.07 | 20.9 | 14.21 | 35.91 | 14.87 | 41.78 | - | VPWF 03 1R PSC | 03SQ | PSC | 787.5 | 1 | 0.5 | 0.07 | 0.045 | 14.21 | 0.295 | 0.25
VPWF 04 1R PSC | 04SQ | PSC | 1 | 941.25 | 1255 | 0.061 | 0.102 | 0.5 | 10 | 0.07 | 20.9 | 14.62 | 39.42 | 15.25 | 45.95 | - | VPWF 04 1R PSC | 04SQ | PSC | 941.25 | 1 | 0.5 | 0.07 | 0.061 | 14.62 | 0.311 | 0.25
VPWF 05 1R PSC | 05SQ | PSC | 1 | 1053.75 | 1405 | 0.075 | 0.125 | 0.5 | 10 | 0.07 | 20.9 | 14.87 | 41.86 | 15.48 | 48.81 | - | VPWF 05 1R PSC | 05SQ | PSC | 1053.75 | 1 | 0.5 | 0.07 | 0.075 | 14.87 | 0.325 | 0.25
VPWF 06 1R PSC | 06SQ | PSC | 1 | 1282.5 | 1710 | 0.066 | 0.11 | 0.5 | 7 | 0.1 | 11.03 | 18.35 | 47.83 | 19.1 | 55.38 | - | VPWF 06 1R PSC | 06SQ | PSC | 1282.5 | 1 | 0.5 | 0.1 | 0.066 | 18.35 | 0.316 | 0.25
VPWF 07 1R PSC | 07SQ | PSC | 1 | 1350 | 1800 | 0.072 | 0.121 | 0.5 | 7.5 | 0.1 | 12.52 | 18.49 | 49.45 | 19.23 | 57.35 | - | VPWF 07 1R PSC | 07SQ | PSC | 1350 | 1 | 0.5 | 0.1 | 0.072 | 18.49 | 0.322 | 0.25
[17 empty] | VPWF 02 1R PSC | 02SQ | PSC | 333.75 | 1 | 5 | 13.02 | 0.012 | 20.43 | 0.262 | 0.25
VPWF - PSC Motor - 2R Coil | [11 empty] | 1+1 | 1+2 | 2+1 | 2+2 |  | VPWF 03 1R PSC | 03SQ | PSC | 787.5 | 1 | 10 | 20.9 | 0.045 | 35.91 | 0.295 | 0.25
Unit Tag | Fan size | Motor Type | Coil Rows | Airflow 1 | Airflow 2 | APD 1 | APD 2 | Fluid Flow | Fluid Flow 2 | WPD 1 | WPD 2 | Capacity 1 | Capacity 2 | Capacity 3 | Capacity 4 |  | VPWF 04 1R PSC | 04SQ | PSC | 941.25 | 1 | 10 | 20.9 | 0.061 | 39.42 | 0.311 | 0.25
VPWF 02 2R PSC | 02SQ | PSC | 2 | 318.75 | 425 | 0.023 | 0.037 | 1 | 1 | 1.21 | 1.21 | 23.1 | 23.1 | 26.87 | 26.87 | - | VPWF 05 1R PSC | 05SQ | PSC | 1053.75 | 1 | 10 | 20.9 | 0.075 | 41.86 | 0.325 | 0.25
VPWF 03 2R PSC | 03SQ | PSC | 2 | 757.5 | 1010 | 0.084 | 0.133 | 1 | 10 | 0.33 | 24.91 | 33.44 | 57.49 | 36.03 | 68.85 | - | VPWF 06 1R PSC | 06SQ | PSC | 1282.5 | 1 | 7 | 11.03 | 0.066 | 47.83 | 0.316 | 0.25
VPWF 04 2R PSC | 04SQ | PSC | 2 | 888.75 | 1185 | 0.108 | 0.174 | 1 | 10 | 0.33 | 24.92 | 34.94 | 63.68 | 37.29 | 75.54 | - | VPWF 07 1R PSC | 07SQ | PSC | 1350 | 1 | 7.5 | 12.52 | 0.072 | 49.45 | 0.322 | 0.25
VPWF 05 2R PSC | 05SQ | PSC | 2 | 982.5 | 1310 | 0.127 | 0.205 | 1 | 10 | 0.33 | 24.92 | 35.81 | 67.73 | 38.01 | 79.84 | - | VPWF 02 1R PSC | 02SQ | PSC | 445 | 1 | 0.5 | 0.21 | 0.019 | 14.23 | 0.269 | 0.25
VPWF 06 2R PSC | 06SQ | PSC | 2 | 1200 | 1600 | 0.114 | 0.184 | 1 | 7 | 0.62 | 18.9 | 40.95 | 77.24 | 43.18 | 90.07 | - | VPWF 03 1R PSC | 03SQ | PSC | 1050 | 1 | 0.5 | 0.07 | 0.074 | 14.87 | 0.324 | 0.25
VPWF 07 2R PSC | 07SQ | PSC | 2 | 1245 | 1660 | 0.121 | 0.195 | 1 | 7.5 | 0.62 | 21.39 | 41.27 | 79.5 | 43.43 | 92.65 | - | VPWF 04 1R PSC | 04SQ | PSC | 1255 | 1 | 0.5 | 0.07 | 0.102 | 15.25 | 0.352 | 0.25
[17 empty] | VPWF 05 1R PSC | 05SQ | PSC | 1405 | 1 | 0.5 | 0.07 | 0.125 | 15.48 | 0.375 | 0.25
VPWF - EC Motor - 1R Coil | [11 empty] | 1+1 | 1+2 | 2+1 | 2+2 |  | VPWF 06 1R PSC | 06SQ | PSC | 1710 | 1 | 0.5 | 0.1 | 0.11 | 19.1 | 0.36 | 0.25
Unit Tag | Fan size | Motor Type | Coil Rows | Airflow 1 | Airflow 2 | APD 1 | APD 2 | Fluid Flow | Fluid Flow 2 | WPD 1 | WPD 2 | Capacity 1 | Capacity 2 | Capacity 3 | Capacity 4 |  | VPWF 07 1R PSC | 07SQ | PSC | 1800 | 1 | 0.5 | 0.1 | 0.121 | 19.23 | 0.371 | 0.25
VPWF 03 1R ECM | 03SQ | ECM | 1 | 791.25 | 1055 | 0.045 | 0.075 | 0.5 | 10 | 0.07 | 20.9 | 14.22 | 35.98 | 14.88 | 41.89 | - | VPWF 02 1R PSC | 02SQ | PSC | 445 | 1 | 5 | 13.03 | 0.019 | 23.58 | 0.269 | 0.25
VPWF 04 1R ECM | 04SQ | ECM | 1 | 1087.5 | 1450 | 0.079 | 0.133 | 0.5 | 10 | 0.07 | 20.9 | 14.94 | 42.58 | 15.54 | 49.64 | - | VPWF 03 1R PSC | 03SQ | PSC | 1050 | 1 | 10 | 20.9 | 0.074 | 41.78 | 0.324 | 0.25
VPWF 05 1R ECM | 05SQ | ECM | 1 | 1245 | 1660 | 0.101 | 0.17 | 0.5 | 10 | 0.07 | 20.91 | 15.23 | 45.75 | 15.81 | 53.38 | - | VPWF 04 1R PSC | 04SQ | PSC | 1255 | 1 | 10 | 20.91 | 0.102 | 45.95 | 0.352 | 0.25
VPWF 06 1R ECM | 06SQ | ECM | 1 | 1462.5 | 1950 | 0.083 | 0.14 | 0.5 | 7 | 0.1 | 11.03 | 18.7 | 51.14 | 19.42 | 59.24 | - | VPWF 05 1R PSC | 05SQ | PSC | 1405 | 1 | 10 | 20.91 | 0.125 | 48.81 | 0.375 | 0.25
[17 empty] | VPWF 06 1R PSC | 06SQ | PSC | 1710 | 1 | 7 | 11.04 | 0.11 | 55.38 | 0.36 | 0.25
VPWF - EC Motor - 2R Coil | [11 empty] | 1+1 | 1+2 | 2+1 | 2+2 |  | VPWF 07 1R PSC | 07SQ | PSC | 1800 | 1 | 7.5 | 12.53 | 0.121 | 57.35 | 0.371 | 0.25
Unit Tag | Fan size | Motor Type | Coil Rows | Airflow 1 | Airflow 2 | APD 1 | APD 2 | Fluid Flow | Fluid Flow 2 | WPD 1 | WPD 2 | Capacity 1 | Capacity 2 | Capacity 3 | Capacity 4 |  | VPWF 02 1R PSC | 02SQ | PSC | 318.75 | 2 | 1 | 1.21 | 0.023 | 23.1 | 0.273 | 0.25
VPWF 03 1R ECM | 03SQ | ECM | 2 | 776.25 | 1035 | 0.087 | 0.139 | 1 | 10 | 0.33 | 24.91 | 33.67 | 58.38 | 36.23 | 69.85 | - | VPWF 03 1R PSC | 03SQ | PSC | 757.5 | 2 | 1 | 0.33 | 0.084 | 33.44 | 0.334 | 0.25
VPWF 04 1R ECM | 04SQ | ECM | 2 | 1061.25 | 1415 | 0.144 | 0.234 | 1 | 10 | 0.33 | 24.92 | 36.43 | 70.88 | 38.53 | 83.19 | - | VPWF 04 1R PSC | 04SQ | PSC | 888.75 | 2 | 1 | 0.33 | 0.108 | 34.94 | 0.358 | 0.25
VPWF 05 1R ECM | 05SQ | ECM | 2 | 1091.25 | 1455 | 0.151 | 0.246 | 1 | 10 | 0.33 | 24.92 | 36.66 | 72.05 | 38.71 | 84.41 | - | VPWF 05 1R PSC | 05SQ | PSC | 982.5 | 2 | 1 | 0.33 | 0.127 | 35.81 | 0.377 | 0.25
VPWF 03 1R ECM | 06SQ | ECM | 2 | 1383.75 | 1845 | 0.144 | 0.234 | 1 | 7 | 0.62 | 18.91 | 42.12 | 83.55 | 44.11 | 96.53 | - | VPWF 06 1R PSC | 06SQ | PSC | 1200 | 2 | 1 | 0.62 | 0.114 | 40.95 | 0.364 | 0.25
[17 empty] | VPWF 07 1R PSC | 07SQ | PSC | 1245 | 2 | 1 | 0.62 | 0.121 | 41.27 | 0.371 | 0.25
[17 empty] | VPWF 02 1R PSC | 02SQ | PSC | 318.75 | 2 | 1 | 1.21 | 0.023 | 23.1 | 0.273 | 0.25
[17 empty] | VPWF 03 1R PSC | 03SQ | PSC | 757.5 | 2 | 10 | 24.91 | 0.084 | 57.49 | 0.334 | 0.25
[17 empty] | VPWF 04 1R PSC | 04SQ | PSC | 888.75 | 2 | 10 | 24.92 | 0.108 | 63.68 | 0.358 | 0.25
[17 empty] | VPWF 05 1R PSC | 05SQ | PSC | 982.5 | 2 | 10 | 24.92 | 0.127 | 67.73 | 0.377 | 0.25
[17 empty] | VPWF 06 1R PSC | 06SQ | PSC | 1200 | 2 | 7 | 18.9 | 0.114 | 77.24 | 0.364 | 0.25
[17 empty] | VPWF 07 1R PSC | 07SQ | PSC | 1245 | 2 | 7.5 | 21.39 | 0.121 | 79.5 | 0.371 | 0.25
[17 empty] | VPWF 02 1R PSC | 02SQ | PSC | 425 | 2 | 1 | 1.22 | 0.037 | 26.87 | 0.287 | 0.25
[17 empty] | VPWF 03 1R PSC | 03SQ | PSC | 1010 | 2 | 1 | 0.33 | 0.133 | 36.03 | 0.383 | 0.25
[17 empty] | VPWF 04 1R PSC | 04SQ | PSC | 1185 | 2 | 1 | 0.33 | 0.174 | 37.29 | 0.424 | 0.25
[17 empty] | VPWF 05 1R PSC | 05SQ | PSC | 1310 | 2 | 1 | 0.33 | 0.205 | 38.01 | 0.455 | 0.25
[17 empty] | VPWF 06 1R PSC | 06SQ | PSC | 1600 | 2 | 1 | 0.63 | 0.184 | 43.18 | 0.434 | 0.25
[17 empty] | VPWF 07 1R PSC | 07SQ | PSC | 1660 | 2 | 1 | 0.63 | 0.195 | 43.43 | 0.445 | 0.25
[17 empty] | VPWF 02 1R PSC | 02SQ | PSC | 425 | 2 | 1 | 1.22 | 0.037 | 26.87 | 0.287 | 0.25
[17 empty] | VPWF 03 1R PSC | 03SQ | PSC | 1010 | 2 | 10 | 24.92 | 0.133 | 68.85 | 0.383 | 0.25
[17 empty] | VPWF 04 1R PSC | 04SQ | PSC | 1185 | 2 | 10 | 24.92 | 0.174 | 75.54 | 0.424 | 0.25
[17 empty] | VPWF 05 1R PSC | 05SQ | PSC | 1310 | 2 | 10 | 24.93 | 0.205 | 79.84 | 0.455 | 0.25
[17 empty] | VPWF 06 1R PSC | 06SQ | PSC | 1600 | 2 | 7 | 18.93 | 0.184 | 90.07 | 0.434 | 0.25
[17 empty] | VPWF 07 1R PSC | 07SQ | PSC | 1660 | 2 | 7.5 | 21.43 | 0.195 | 92.65 | 0.445 | 0.25
VPWF - EC Motor
[17 empty] | Unit Tag | Fan size |  | Airflow | Coil Rows | Fluid Flow | WPD | APD | Capacity | Fan TSP | Downstream SP
[17 empty] | VPWF 03 1R ECM | 03SQ | ECM | 791.25 | 1 | 0.5 | 0.07 | 0.045 | 14.22 | 0.295 | 0.25
[17 empty] | VPWF 04 1R ECM | 04SQ | ECM | 1087.5 | 1 | 0.5 | 0.07 | 0.079 | 14.94 | 0.329 | 0.25
[17 empty] | VPWF 05 1R ECM | 05SQ | ECM | 1245 | 1 | 0.5 | 0.07 | 0.101 | 15.23 | 0.351 | 0.25
[17 empty] | VPWF 06 1R ECM | 06SQ | ECM | 1462.5 | 1 | 0.5 | 0.1 | 0.083 | 18.7 | 0.333 | 0.25
[17 empty] | VPWF 03 1R ECM | 03SQ | ECM | 791.25 | 1 | 10 | 20.9 | 0.045 | 35.98 | 0.295 | 0.25
[17 empty] | VPWF 04 1R ECM | 04SQ | ECM | 1087.5 | 1 | 10 | 20.9 | 0.079 | 42.58 | 0.329 | 0.25
[17 empty] | VPWF 05 1R ECM | 05SQ | ECM | 1245 | 1 | 10 | 20.91 | 0.101 | 45.75 | 0.351 | 0.25
[17 empty] | VPWF 06 1R ECM | 06SQ | ECM | 1462.5 | 1 | 7 | 11.03 | 0.083 | 51.14 | 0.333 | 0.25
[17 empty] | VPWF 03 1R ECM | 03SQ | ECM | 1055 | 1 | 0.5 | 0.07 | 0.075 | 14.88 | 0.325 | 0.25
[17 empty] | VPWF 04 1R ECM | 04SQ | ECM | 1450 | 1 | 0.5 | 0.07 | 0.133 | 15.54 | 0.383 | 0.25
[17 empty] | VPWF 05 1R ECM | 05SQ | ECM | 1660 | 1 | 0.5 | 0.07 | 0.17 | 15.81 | 0.42 | 0.25
[17 empty] | VPWF 06 1R ECM | 06SQ | ECM | 1950 | 1 | 0.5 | 0.1 | 0.14 | 19.42 | 0.39 | 0.25
[17 empty] | VPWF 03 1R ECM | 03SQ | ECM | 1055 | 1 | 10 | 20.9 | 0.075 | 41.89 | 0.325 | 0.25
[17 empty] | VPWF 04 1R ECM | 04SQ | ECM | 1450 | 1 | 10 | 20.91 | 0.133 | 49.64 | 0.383 | 0.25
[17 empty] | VPWF 05 1R ECM | 05SQ | ECM | 1660 | 1 | 10 | 20.91 | 0.17 | 53.38 | 0.42 | 0.25
[17 empty] | VPWF 06 1R ECM | 06SQ | ECM | 1950 | 1 | 7 | 11.05 | 0.14 | 59.24 | 0.39 | 0.25
[17 empty] | VPWF 03 1R ECM | 03SQ | ECM | 776.25 | 2 | 1 | 0.33 | 0.087 | 33.67 | 0.337 | 0.25
[17 empty] | VPWF 04 1R ECM | 04SQ | ECM | 1061.25 | 2 | 1 | 0.33 | 0.144 | 36.43 | 0.394 | 0.25
[17 empty] | VPWF 05 1R ECM | 05SQ | ECM | 1091.25 | 2 | 1 | 0.33 | 0.151 | 36.66 | 0.401 | 0.25
[17 empty] | VPWF 06 1R ECM | 06SQ | ECM | 1383.75 | 2 | 1 | 0.62 | 0.144 | 42.12 | 0.394 | 0.25
[17 empty] | VPWF 03 1R ECM | 03SQ | ECM | 776.25 | 2 | 10 | 24.91 | 0.087 | 58.38 | 0.337 | 0.25
[17 empty] | VPWF 04 1R ECM | 04SQ | ECM | 1061.25 | 2 | 10 | 24.92 | 0.144 | 70.88 | 0.394 | 0.25
[17 empty] | VPWF 05 1R ECM | 05SQ | ECM | 1091.25 | 2 | 10 | 24.92 | 0.151 | 72.05 | 0.401 | 0.25
[17 empty] | VPWF 06 1R ECM | 06SQ | ECM | 1383.75 | 2 | 7 | 18.91 | 0.144 | 83.55 | 0.394 | 0.25
[17 empty] | VPWF 03 1R ECM | 03SQ | ECM | 1035 | 2 | 1 | 0.33 | 0.139 | 36.23 | 0.389 | 0.25
[17 empty] | VPWF 04 1R ECM | 04SQ | ECM | 1415 | 2 | 1 | 0.33 | 0.234 | 38.53 | 0.484 | 0.25
[17 empty] | VPWF 05 1R ECM | 05SQ | ECM | 1455 | 2 | 1 | 0.33 | 0.246 | 38.71 | 0.496 | 0.25
[17 empty] | VPWF 06 1R ECM | 06SQ | ECM | 1845 | 2 | 1 | 0.63 | 0.234 | 44.11 | 0.484 | 0.25
[17 empty] | VPWF 03 1R ECM | 03SQ | ECM | 1035 | 2 | 10 | 24.92 | 0.139 | 69.85 | 0.389 | 0.25
[17 empty] | VPWF 04 1R ECM | 04SQ | ECM | 1415 | 2 | 10 | 24.93 | 0.234 | 83.19 | 0.484 | 0.25
[17 empty] | VPWF 05 1R ECM | 05SQ | ECM | 1455 | 2 | 10 | 24.93 | 0.246 | 84.41 | 0.496 | 0.25
[17 empty] | VPWF 06 1R ECM | 06SQ | ECM | 1845 | 2 | 7 | 18.96 | 0.234 | 96.53 | 0.484 | 0.25

## VSWF Data (hidden)
VSWF - PSC Motor - 1R Coil | [11 empty] | 1+1 | 1+2 | 2+1 | 2+2 |  | VPWF - PSC Motor
Unit Tag | Fan size | Motor Type | Coil Rows | Airflow 1 | Airflow 2 | APD 1 | APD 2 | Fluid Flow 1 | Fluid Flow 2 | WPD 1 | WPD 2 | Capacity 1 | Capacity 2 | Capacity 3 | Capacity 4 |  | Unit Tag | Fan size | Motor Type | Valve Airflow | Fan Airflow | Coil Rows | Fluid Flow | WPD | APD | Capacity | Fan TSP | Downstream SP
VSWF 02 1R PSC | 02SQ | PSC | 1 | 483.75 | 645 | 0.055 | 0.091 | 0.5 | 5 | 0.15 | 9.01 | 12.4 | 20.69 | 13.43 | 24.05 | - | VSWF 02 1R PSC | 02SQ | PSC | 241.875 | 483.75 | 1 | 0.5 | 0.15 | 0.055 | 12.4 | 0.305 | 0.25
VSWF 03 1R PSC | 03SQ | PSC | 1 | 862.5 | 1150 | 0.06 | 0.1 | 0.5 | 8 | 0.07 | 13.44 | 14.99 | 38.64 | 15.64 | 44.88 | - | VSWF 03 1R PSC | 03SQ | PSC | 431.25 | 862.5 | 1 | 0.5 | 0.07 | 0.06 | 14.99 | 0.31 | 0.25
VSWF 04 1R PSC | 04SQ | PSC | 1 | 1117.5 | 1490 | 0.095 | 0.16 | 0.5 | 8 | 0.07 | 13.44 | 15.58 | 44.22 | 16.2 | 51.41 | - | VSWF 04 1R PSC | 04SQ | PSC | 558.75 | 1117.5 | 1 | 0.5 | 0.07 | 0.095 | 15.58 | 0.345 | 0.25
VSWF 05 1R PSC | 05SQ | PSC | 1 | 1305 | 1740 | 0.11 | 0.186 | 0.5 | 8 | 0.08 | 14.11 | 17.32 | 52.94 | 17.91 | 61.41 | - | VSWF 05 1R PSC | 05SQ | PSC | 652.5 | 1305 | 1 | 0.5 | 0.08 | 0.11 | 17.32 | 0.36 | 0.25
VSWF 06 1R PSC | 06SQ | PSC | 1 | 1852.5 | 2470 | 0.11 | 0.186 | 0.5 | 6 | 0.11 | 9.16 | 21.35 | 64.92 | 22.01 | 74.87 | - | VSWF 06 1R PSC | 06SQ | PSC | 926.25 | 1852.5 | 1 | 0.5 | 0.11 | 0.11 | 21.35 | 0.36 | 0.25
VSWF 07 1R PSC | 07SQ | PSC | 1 | 2006.25 | 2675 | 0.127 | 0.215 | 0.5 | 6 | 0.11 | 9.17 | 21.54 | 67.54 | 22.18 | 77.86 | - | VSWF 07 1R PSC | 07SQ | PSC | 1003.125 | 2006.25 | 1 | 0.5 | 0.11 | 0.127 | 21.54 | 0.377 | 0.25
[17 empty] | VSWF 02 1R PSC | 02SQ | PSC | 241.875 | 483.75 | 1 | 5 | 9.01 | 0.055 | 20.69 | 0.305 | 0.25
VSWF - PSC Motor - 2R Coil | [11 empty] | 1+1 | 1+2 | 2+1 | 2+2 |  | VSWF 03 1R PSC | 03SQ | PSC | 431.25 | 862.5 | 1 | 8 | 13.44 | 0.06 | 38.64 | 0.31 | 0.25
Unit Tag | Fan size | Motor Type | Coil Rows | Airflow 1 | Airflow 2 | APD 1 | APD 2 | Fluid Flow | Fluid Flow 2 | WPD 1 | WPD 2 | Capacity 1 | Capacity 2 | Capacity 3 | Capacity 4 |  | VSWF 04 1R PSC | 04SQ | PSC | 558.75 | 1117.5 | 1 | 8 | 13.44 | 0.095 | 44.22 | 0.345 | 0.25
VSWF 02 2R PSC | 02SQ | PSC | 2 | 450 | 600 | 0.095 | 0.153 | 1 | 5 | 0.93 | 16.25 | 25.09 | 33.15 | 28.01 | 39.25 | - | VSWF 05 1R PSC | 05SQ | PSC | 652.5 | 1305 | 1 | 8 | 14.11 | 0.11 | 52.94 | 0.36 | 0.25
VSWF 03 2R PSC | 03SQ | PSC | 2 | 832.5 | 1110 | 0.112 | 0.18 | 1 | 8 | 0.37 | 17.62 | 35.95 | 63.08 | 38.48 | 74.59 | - | VSWF 06 1R PSC | 06SQ | PSC | 926.25 | 1852.5 | 1 | 6 | 9.16 | 0.11 | 64.92 | 0.36 | 0.25
VSWF 04 2R PSC | 04SQ | PSC | 2 | 1068.75 | 1425 | 0.169 | 0.275 | 1 | 8 | 0.37 | 17.63 | 38.17 | 73.04 | 40.33 | 85.04 | - | VSWF 07 1R PSC | 07SQ | PSC | 1003.125 | 2006.25 | 1 | 6 | 9.17 | 0.127 | 67.54 | 0.377 | 0.25
VSWF 05 2R PSC | 05SQ | PSC | 2 | 1230 | 1640 | 0.187 | 0.306 | 1 | 8 | 0.37 | 17.37 | 42.27 | 86.12 | 44.36 | 100.46 | - | VSWF 02 1R PSC | 02SQ | PSC | 322.5 | 645 | 1 | 0.5 | 0.15 | 0.091 | 13.43 | 0.341 | 0.25
VSWF 06 2R PSC | 06SQ | PSC | 2 | 1751.25 | 2335 | 0.187 | 0.303 | 1.5 | 6 | 1.46 | 16.74 | 63.82 | 105.12 | 67.47 | 119.57 | - | VSWF 03 1R PSC | 03SQ | PSC | 575 | 1150 | 1 | 0.5 | 0.07 | 0.1 | 15.64 | 0.35 | 0.25
VSWF 07 2R PSC | 07SQ | PSC | 2 | 1833.75 | 2445 | 0.202 | 0.328 | 1.5 | 6 | 1.46 | 16.74 | 64.45 | 107.45 | 67.99 | 121.85 | - | VSWF 04 1R PSC | 04SQ | PSC | 745 | 1490 | 1 | 0.5 | 0.07 | 0.16 | 16.2 | 0.41 | 0.25
[17 empty] | VSWF 05 1R PSC | 05SQ | PSC | 870 | 1740 | 1 | 0.5 | 0.08 | 0.186 | 17.91 | 0.436 | 0.25
VSWF - EC Motor - 1R Coil | [11 empty] | 1+1 | 1+2 | 2+1 | 2+2 |  | VSWF 06 1R PSC | 06SQ | PSC | 1235 | 2470 | 1 | 0.5 | 0.11 | 0.186 | 22.01 | 0.436 | 0.25
Unit Tag | Fan size | Motor Type | Coil Rows | Airflow 1 | Airflow 2 | APD 1 | APD 2 | Fluid Flow | Fluid Flow 2 | WPD 1 | WPD 2 | Capacity 1 | Capacity 2 | Capacity 3 | Capacity 4 |  | VSWF 07 1R PSC | 07SQ | PSC | 1337.5 | 2675 | 1 | 0.5 | 0.11 | 0.215 | 22.18 | 0.465 | 0.25
VSWF 03 1R ECM | 03SQ | ECM | 1 | 821.25 | 1095 | 0.055 | 0.092 | 0.5 | 8 | 0.07 | 13.44 | 14.87 | 37.66 | 15.54 | 43.75 | - | VSWF 02 1R PSC | 02SQ | PSC | 322.5 | 645 | 1 | 5 | 9.02 | 0.091 | 24.05 | 0.341 | 0.25
VSWF 04 1R ECM | 04SQ | ECM | 1 | 1121.25 | 1495 | 0.096 | 0.161 | 0.5 | 8 | 0.07 | 13.44 | 15.59 | 44.29 | 16.21 | 51.5 | - | VSWF 03 1R PSC | 03SQ | PSC | 575 | 1150 | 1 | 8 | 13.44 | 0.1 | 44.88 | 0.35 | 0.25
VSWF 05 1R ECM | 05SQ | ECM | 1 | 1526.25 | 2035 | 0.146 | 0.249 | 0.5 | 8 | 0.08 | 14.12 | 17.64 | 57.39 | 18.21 | 66.59 | - | VSWF 04 1R PSC | 04SQ | PSC | 745 | 1490 | 1 | 8 | 13.44 | 0.16 | 51.41 | 0.41 | 0.25
VSWF 06 1R ECM | 06SQ | ECM | 1 | 1860 | 2480 | 0.111 | 0.187 | 0.5 | 6 | 0.11 | 9.16 | 21.36 | 65.05 | 22.02 | 75.02 | - | VSWF 05 1R PSC | 05SQ | PSC | 870 | 1740 | 1 | 8 | 14.12 | 0.186 | 61.41 | 0.436 | 0.25
[17 empty] | VSWF 06 1R PSC | 06SQ | PSC | 1235 | 2470 | 1 | 6 | 9.18 | 0.186 | 74.87 | 0.436 | 0.25
VSWF - EC Motor - 2R Coil | [11 empty] | 1+1 | 1+2 | 2+1 | 2+2 |  | VSWF 07 1R PSC | 07SQ | PSC | 1337.5 | 2675 | 1 | 6 | 9.19 | 0.215 | 77.86 | 0.465 | 0.25
Unit Tag | Fan size | Motor Type | Coil Rows | Airflow 1 | Airflow 2 | APD 1 | APD 2 | Fluid Flow | Fluid Flow 2 | WPD 1 | WPD 2 | Capacity 1 | Capacity 2 | Capacity 3 | Capacity 4 |  | VSWF 02 2R PSC | 02SQ | PSC | 225 | 450 | 2 | 1 | 0.93 | 0.095 | 25.09 | 0.345 | 0.25
VSWF 03 2R ECM | 03SQ | ECM | 2 | 821.25 | 1095 | 0.11 | 0.176 | 1 | 8 | 0.37 | 17.62 | 35.82 | 62.53 | 38.37 | 74.03 | - | VSWF 03 2R PSC | 03SQ | PSC | 416.25 | 832.5 | 2 | 1 | 0.37 | 0.112 | 35.95 | 0.362 | 0.25
VSWF 04 2R ECM | 04SQ | ECM | 2 | 1008.75 | 1345 | 0.154 | 0.249 | 1 | 8 | 0.37 | 17.63 | 37.69 | 70.68 | 39.93 | 82.6 | - | VSWF 04 2R PSC | 04SQ | PSC | 534.375 | 1068.75 | 2 | 1 | 0.37 | 0.169 | 38.17 | 0.419 | 0.25
VSWF 05 2R ECM | 05SQ | ECM | 2 | 1098.75 | 1465 | 0.156 | 0.252 | 1.5 | 8 | 0.76 | 17.37 | 52.53 | 80.67 | 56.9 | 94.78 | - | VSWF 05 2R PSC | 05SQ | PSC | 615 | 1230 | 2 | 1 | 0.37 | 0.187 | 42.27 | 0.437 | 0.25
VSWF 06 2R ECM | 06SQ | ECM | 2 | 1567.5 | 2090 | 0.156 | 0.251 | 1.5 | 6 | 1.46 | 16.72 | 62.21 | 99.54 | 66.15 | 114.03 | - | VSWF 06 2R PSC | 06SQ | PSC | 875.625 | 1751.25 | 2 | 1.5 | 1.46 | 0.187 | 63.82 | 0.437 | 0.25
[17 empty] | VSWF 07 2R PSC | 07SQ | PSC | 916.875 | 1833.75 | 2 | 1.5 | 1.46 | 0.202 | 64.45 | 0.452 | 0.25
[17 empty] | VSWF 02 2R PSC | 02SQ | PSC | 225 | 450 | 2 | 5 | 16.25 | 0.095 | 33.15 | 0.345 | 0.25
[17 empty] | VSWF 03 2R PSC | 03SQ | PSC | 416.25 | 832.5 | 2 | 8 | 17.62 | 0.112 | 63.08 | 0.362 | 0.25
[17 empty] | VSWF 04 2R PSC | 04SQ | PSC | 534.375 | 1068.75 | 2 | 8 | 17.63 | 0.169 | 73.04 | 0.419 | 0.25
[17 empty] | VSWF 05 2R PSC | 05SQ | PSC | 615 | 1230 | 2 | 8 | 17.37 | 0.187 | 86.12 | 0.437 | 0.25
[17 empty] | VSWF 06 2R PSC | 06SQ | PSC | 875.625 | 1751.25 | 2 | 6 | 16.74 | 0.187 | 105.12 | 0.437 | 0.25
[17 empty] | VSWF 07 2R PSC | 07SQ | PSC | 916.875 | 1833.75 | 2 | 6 | 16.74 | 0.202 | 107.45 | 0.452 | 0.25
[17 empty] | VSWF 02 2R PSC | 02SQ | PSC | 300 | 600 | 2 | 1 | 0.94 | 0.153 | 28.01 | 0.403 | 0.25
[17 empty] | VSWF 03 2R PSC | 03SQ | PSC | 555 | 1110 | 2 | 1 | 0.37 | 0.18 | 38.48 | 0.43 | 0.25
[17 empty] | VSWF 04 2R PSC | 04SQ | PSC | 712.5 | 1425 | 2 | 1 | 0.37 | 0.275 | 40.33 | 0.525 | 0.25
[17 empty] | VSWF 05 2R PSC | 05SQ | PSC | 820 | 1640 | 2 | 1 | 0.37 | 0.306 | 44.36 | 0.556 | 0.25
[17 empty] | VSWF 06 2R PSC | 06SQ | PSC | 1167.5 | 2335 | 2 | 1.5 | 1.47 | 0.303 | 67.47 | 0.553 | 0.25
[17 empty] | VSWF 07 2R PSC | 07SQ | PSC | 1222.5 | 2445 | 2 | 1.5 | 1.47 | 0.328 | 67.99 | 0.578 | 0.25
[17 empty] | VSWF 02 2R PSC | 02SQ | PSC | 300 | 600 | 2 | 5 | 16.27 | 0.153 | 39.25 | 0.403 | 0.25
[17 empty] | VSWF 03 2R PSC | 03SQ | PSC | 555 | 1110 | 2 | 8 | 17.63 | 0.18 | 74.59 | 0.43 | 0.25
[17 empty] | VSWF 04 2R PSC | 04SQ | PSC | 712.5 | 1425 | 2 | 8 | 17.64 | 0.275 | 85.04 | 0.525 | 0.25
[17 empty] | VSWF 05 2R PSC | 05SQ | PSC | 820 | 1640 | 2 | 8 | 17.38 | 0.306 | 100.46 | 0.556 | 0.25
[17 empty] | VSWF 06 2R PSC | 06SQ | PSC | 1167.5 | 2335 | 2 | 6 | 16.79 | 0.303 | 119.57 | 0.553 | 0.25
[17 empty] | VSWF 07 2R PSC | 07SQ | PSC | 1222.5 | 2445 | 2 | 6 | 16.79 | 0.328 | 121.85 | 0.578 | 0.25
VPWF - EC Motor
[17 empty] | Unit Tag | Fan size | Motor Type | Valve Airflow | Fan Airflow | Coil Rows | Fluid Flow | WPD | APD | Capacity | Fan TSP | Downstream SP
[17 empty] | VSWF 03 1R ECM | 03SQ | ECM | 410.625 | 821.25 | 1 | 0.5 | 0.07 | 0.055 | 14.87 | 0.305 | 0.25
[17 empty] | VSWF 04 1R ECM | 04SQ | ECM | 560.625 | 1121.25 | 1 | 0.5 | 0.07 | 0.096 | 15.59 | 0.346 | 0.25
[17 empty] | VSWF 05 1R ECM | 05SQ | ECM | 763.125 | 1526.25 | 1 | 0.5 | 0.08 | 0.146 | 17.64 | 0.396 | 0.25
[17 empty] | VSWF 06 1R ECM | 06SQ | ECM | 930 | 1860 | 1 | 0.5 | 0.11 | 0.111 | 21.36 | 0.361 | 0.25
[17 empty] | VSWF 03 1R ECM | 03SQ | ECM | 410.625 | 821.25 | 1 | 8 | 13.44 | 0.055 | 37.66 | 0.305 | 0.25
[17 empty] | VSWF 04 1R ECM | 04SQ | ECM | 560.625 | 1121.25 | 1 | 8 | 13.44 | 0.096 | 44.29 | 0.346 | 0.25
[17 empty] | VSWF 05 1R ECM | 05SQ | ECM | 763.125 | 1526.25 | 1 | 8 | 14.12 | 0.146 | 57.39 | 0.396 | 0.25
[17 empty] | VSWF 06 1R ECM | 06SQ | ECM | 930 | 1860 | 1 | 6 | 9.16 | 0.111 | 65.05 | 0.361 | 0.25
[17 empty] | VSWF 03 1R ECM | 03SQ | ECM | 547.5 | 1095 | 1 | 0.5 | 0.07 | 0.092 | 15.54 | 0.342 | 0.25
[17 empty] | VSWF 04 1R ECM | 04SQ | ECM | 747.5 | 1495 | 1 | 0.5 | 0.07 | 0.161 | 16.21 | 0.411 | 0.25
[17 empty] | VSWF 05 1R ECM | 05SQ | ECM | 1017.5 | 2035 | 1 | 0.5 | 0.08 | 0.249 | 18.21 | 0.499 | 0.25
[17 empty] | VSWF 06 1R ECM | 06SQ | ECM | 1240 | 2480 | 1 | 0.5 | 0.11 | 0.187 | 22.02 | 0.437 | 0.25
[17 empty] | VSWF 03 1R ECM | 03SQ | ECM | 547.5 | 1095 | 1 | 8 | 13.44 | 0.092 | 43.75 | 0.342 | 0.25
[17 empty] | VSWF 04 1R ECM | 04SQ | ECM | 747.5 | 1495 | 1 | 8 | 13.44 | 0.161 | 51.5 | 0.411 | 0.25
[17 empty] | VSWF 05 1R ECM | 05SQ | ECM | 1017.5 | 2035 | 1 | 8 | 14.12 | 0.249 | 66.59 | 0.499 | 0.25
[17 empty] | VSWF 06 1R ECM | 06SQ | ECM | 1240 | 2480 | 1 | 6 | 9.18 | 0.187 | 75.02 | 0.437 | 0.25
[17 empty] | VSWF 03 2R ECM | 03SQ | ECM | 410.625 | 821.25 | 2 | 1 | 0.37 | 0.11 | 35.82 | 0.36 | 0.25
[17 empty] | VSWF 04 2R ECM | 04SQ | ECM | 504.375 | 1008.75 | 2 | 1 | 0.37 | 0.154 | 37.69 | 0.404 | 0.25
[17 empty] | VSWF 05 2R ECM | 05SQ | ECM | 549.375 | 1098.75 | 2 | 1.5 | 0.76 | 0.156 | 52.53 | 0.406 | 0.25
[17 empty] | VSWF 06 2R ECM | 06SQ | ECM | 783.75 | 1567.5 | 2 | 1.5 | 1.46 | 0.156 | 62.21 | 0.406 | 0.25
[17 empty] | VSWF 03 2R ECM | 03SQ | ECM | 410.625 | 821.25 | 2 | 8 | 17.62 | 0.11 | 62.53 | 0.36 | 0.25
[17 empty] | VSWF 04 2R ECM | 04SQ | ECM | 504.375 | 1008.75 | 2 | 8 | 17.63 | 0.154 | 70.68 | 0.404 | 0.25
[17 empty] | VSWF 05 2R ECM | 05SQ | ECM | 549.375 | 1098.75 | 2 | 8 | 17.37 | 0.156 | 80.67 | 0.406 | 0.25
[17 empty] | VSWF 06 2R ECM | 06SQ | ECM | 783.75 | 1567.5 | 2 | 6 | 16.72 | 0.156 | 99.54 | 0.406 | 0.25
[17 empty] | VSWF 03 2R ECM | 03SQ | ECM | 547.5 | 1095 | 2 | 1 | 0.37 | 0.176 | 38.37 | 0.426 | 0.25
[17 empty] | VSWF 04 2R ECM | 04SQ | ECM | 672.5 | 1345 | 2 | 1 | 0.37 | 0.249 | 39.93 | 0.499 | 0.25
[17 empty] | VSWF 05 2R ECM | 05SQ | ECM | 732.5 | 1465 | 2 | 1.5 | 0.77 | 0.252 | 56.9 | 0.502 | 0.25
[17 empty] | VSWF 06 2R ECM | 06SQ | ECM | 1045 | 2090 | 2 | 1.5 | 1.47 | 0.251 | 66.15 | 0.501 | 0.25
[17 empty] | VSWF 03 2R ECM | 03SQ | ECM | 547.5 | 1095 | 2 | 8 | 17.63 | 0.176 | 74.03 | 0.426 | 0.25
[17 empty] | VSWF 04 2R ECM | 04SQ | ECM | 672.5 | 1345 | 2 | 8 | 17.64 | 0.249 | 82.6 | 0.499 | 0.25
[17 empty] | VSWF 05 2R ECM | 05SQ | ECM | 732.5 | 1465 | 2 | 8 | 17.38 | 0.252 | 94.78 | 0.502 | 0.25
[17 empty] | VSWF 06 2R ECM | 06SQ | ECM | 1045 | 2090 | 2 | 6 | 16.77 | 0.251 | 114.03 | 0.501 | 0.25

## FP Acoustics (hidden)
VPCF |  |  |  | 30% | of fan airflow |  | NC (No Suppressor) |  |  |  | NC (Suppressor) | [6 empty] | VSCF |  |  |  | 30% | of fan airflow |  | NC (No Suppressor) |  |  | NC (Suppressor)
Fan Size | Motor Type | Valve Size | Design Valve Airflow | Min Valve Airflow | Fan Airflow | Airflow Point | Radiated Valve | Discharge Valve | Radiated Fan | Discharge Fan | Radiated Valve | Discharge Valve | Radiated Fan | Discharge Fan |  |  |  | Fan Size | Motor Type | Valve Size | Design Valve Airflow | Min Valve Airflow | Fan Airflow | Airflow Point | Radiated Fan | Radiated Valve&Fan | Discharge Fan | Radiated Fan | Radiated Valve&Fan | Discharge Fan
02SQ | PSC | 5" (127mm) | 162 | 40 | 122 | Min | 15 | 15 | 26 | 15 | 15 | 15 | 22 | 15 | 32.79% | 36.6 | -3.4 | 02SQ | PSC | 4" (102 mm) | 190 | 57 | 190 | Min | 21 | 24 | 16 | 17 | 20 | 16
03SQ | PSC | 6" (152mm) | 327.6 | 75.6 | 252 | Min | 16 | 15 | 27 | 15 | 16 | 15 | 22 | 15 | 30% | 75.6 | 0 | 03SQ | PSC | 6" (152mm) | 254 | 76.2 | 254 | Min | 21 | 25 | 15 | 11 | 20 | 15
04SQ | PSC | 8" (203mm) | 405 | 105 | 300 | Min | 20 | 15 | 28 | 15 | 20 | 15 | 22 | 15 | 35% | 90 | -15 | 04SQ | PSC | 6" (152mm) | 330 | 99 | 330 | Min | 22 | 26 | 15 | 16 | 24 | 15
05SQ | PSC | 10" (254mm) | 515 | 165 | 350 | Min | 22 | 15 | 28 | 15 | 22 | 15 | 25 | 15 | 47.14% | 105 | -60 | 05SQ | PSC | 10" (254mm) | 405 | 165 | 405 | Min | 25 | 25 | 15 | 13 | 19 | 15
06SQ | PSC | 10" (254mm) | 1144 | 264 | 880 | Min | 24 | 17 | 37 | 17 | 24 | 17 | 35 | 17 | 30% | 264 | 0 | 06SQ | PSC | 10" (254mm) | 700 | 210 | 700 | Min | 26 | 33 | 15 | 19 | 31 | 15
07SQ | PSC | 10" (254mm) | 1300 | 300 | 1000 | Min | 26 | 20 | 37 | 17 | 26 | 20 | 30 | 17 | 30% | 300 | 0 | 07SQ | PSC | 10" (254mm) | 850 | 255 | 850 | Min | 26 | 32 | 17 | 18 | 29 | 17
03SQ | ECM | 6" (152mm) | 228 | 60 | 168 | Min | 15 | 15 | 28 | 15 | 15 | 15 | 22 | 15 | 35.71% | 50.4 | -9.6 | 03SQ | ECM | 6" (152mm) | 201 | 60.3 | 201 | Min | 22 | 24 | 15 | 10 | 13 | 15
04SQ | ECM | 8" (203mm) | 327 | 105 | 222 | Min | 19 | 15 | 27 | 15 | 19 | 15 | 21 | 15 | 47.3% | 66.6 | -38.4 | 04SQ | ECM | 6" (152mm) | 263 | 78.9 | 263 | Min | 22 | 24 | 15 | 11 | 17 | 15
05SQ | ECM | 10" (254mm) | 446 | 165 | 281 | Min | 21 | 15 | 30 | 15 | 21 | 15 | 26 | 15 | 58.72% | 84.3 | -80.7 | 05SQ | ECM | 10" (254mm) | 350 | 165 | 350 | Min | 21 | 23 | 15 | 11 | 16 | 15
06SQ | ECM | 10" (254mm) | 1163.5 | 268.5 | 895 | Min | 24 | 17 | 38 | 19 | 24 | 17 | 37 | 19 | 30% | 268.5 | 0 | 06SQ | ECM | 10" (254mm) | 700 | 210 | 700 | Min | 24 | 33 | 15 | 16 | 31 | 15
02SQ | PSC | 6" (152mm) | 475.8 | 109.8 | 366 | 50% | 23 | 19 | 30 | 15 | 23 | 19 | 29 | 15 | 30% | 109.8 | 0 | 02SQ | PSC | 5" (127mm) | 305 | 91.5 | 305 | 50% | 22 | 27 | 17 | 19 | 25 | 17
03SQ | PSC | 10" (254mm) | 928.2 | 214.2 | 714 | 50% | 26 | 16 | 37 | 19 | 26 | 16 | 35 | 19 | 30% | 214.2 | 0 | 03SQ | PSC | 8" (203mm) | 525 | 157.5 | 525 | 50% | 26 | 28 | 15 | 16 | 25 | 15
04SQ | PSC | 10" (254mm) | 1137.5 | 262.5 | 875 | 50% | 27 | 19 | 36 | 17 | 27 | 19 | 34 | 17 | 30% | 262.5 | 0 | 04SQ | PSC | 8" (203mm) | 650 | 195 | 650 | 50% | 27 | 31 | 15 | 20 | 26 | 15
05SQ | PSC | 10" (254mm) | 1319.5 | 304.5 | 1015 | 50% | 30 | 21 | 37 | 17 | 30 | 21 | 31 | 17 | 30% | 304.5 | 0 | 05SQ | PSC | 10" (254mm) | 875 | 262.5 | 875 | 50% | 30 | 33 | 15 | 21 | 26 | 15
06SQ | PSC | 12" (305mm) | 1937 | 447 | 1490 | 50% | 31 | 24 | 42 | 24 | 31 | 24 | 40 | 24 | 30% | 447 | 0 | 06SQ | PSC | 10" (254mm) | 1050 | 315 | 1050 | 50% | 31 | 33 | 15 | 20 | 30 | 15
07SQ | PSC | 14" (356mm) | 2132 | 492 | 1640 | 50% | 30 | 21 | 44 | 26 | 30 | 21 | 35 | 26 | 30% | 492 | 0 | 07SQ | PSC | 10" (254mm) | 1230 | 369 | 1230 | 50% | 31 | 36 | 22 | 23 | 31 | 22
03SQ | ECM | 8" (203mm) | 811.2 | 187.2 | 624 | 50% | 26 | 19 | 35 | 22 | 26 | 19 | 34 | 22 | 30% | 187.2 | 0 | 03SQ | ECM | 6" (152mm) | 450 | 135 | 450 | 50% | 25 | 28 | 15 | 13 | 24 | 15
04SQ | ECM | 10" (254mm) | 1125.8 | 259.8 | 866 | 50% | 27 | 19 | 36 | 15 | 27 | 19 | 31 | 15 | 30% | 259.8 | 0 | 04SQ | ECM | 8" (203mm) | 630 | 189 | 630 | 50% | 26 | 31 | 15 | 15 | 26 | 15
05SQ | ECM | 10" (254mm) | 1385.8 | 319.8 | 1066 | 50% | 31 | 22 | 38 | 19 | 31 | 22 | 31 | 19 | 30% | 319.8 | 0 | 05SQ | ECM | 10" (254mm) | 850 | 255 | 850 | 50% | 27 | 33 | 15 | 17 | 26 | 15
06SQ | ECM | 14" (356mm) | 2021.5 | 466.5 | 1555 | 50% | 29 | 21 | 44 | 26 | 29 | 21 | 43 | 26 | 30% | 466.5 | 0 | 06SQ | ECM | 10" (254mm) | 900 | 270 | 900 | 50% | 26 | 33 | 15 | 16 | 30 | 15
02SQ | PSC | 8" (203mm) | 591.5 | 136.5 | 455 | Max | 22 | 16 | 33 | 17 | 22 | 16 | 31 | 17 | 30% | 136.5 | 0 | 02SQ | PSC | 8" (203mm) | 695 | 208.5 | 695 | Max | 34 | 37 | 31 | 30 | 33 | 31
03SQ | PSC | 12" (305mm) | 1423.5 | 328.5 | 1095 | Max | 31 | 19 | 40 | 22 | 31 | 19 | 39 | 22 | 30% | 328.5 | 0 | 03SQ | PSC | 10" (254mm) | 1185 | 355.5 | 1185 | Max | 40 | 40 | 29 | 38 | 38 | 29
04SQ | PSC | 12" (305mm) | 1722.5 | 397.5 | 1325 | Max | 34 | 21 | 43 | 24 | 34 | 21 | 40 | 24 | 30% | 397.5 | 0 | 04SQ | PSC | 12" (305mm) | 1555 | 466.5 | 1555 | Max | 42 | 44 | 30 | 39 | 40 | 30
05SQ | PSC | 14" (356mm) | 2002 | 462 | 1540 | Max | 34 | 21 | 44 | 24 | 34 | 21 | 39 | 24 | 30% | 462 | 0 | 05SQ | PSC | 14" (356mm) | 1900 | 570 | 1900 | Max | 44 | 45 | 33 | 38 | 39 | 33
06SQ | PSC | 14" (356mm) | 2437.5 | 562.5 | 1875 | Max | 32 | 24 | 45 | 29 | 32 | 24 | 44 | 29 | 30% | 562.5 | 0 | 06SQ | PSC | 14" (356mm) | 2625 | 787.5 | 2625 | Max | 46 | 48 | 33 | 38 | 44 | 33
07SQ | PSC | 14" (356mm) | 2626 | 606 | 2020 | Max | 35 | 25 | 45 | 27 | 35 | 25 | 39 | 27 | 30% | 606 | 0 | 07SQ | PSC | 16" (406mm) | 3015 | 904.5 | 3015 | Max | 48 | 51 | 36 | 37 | 40 | 36
03SQ | ECM | 10" (254mm) | 1397.5 | 322.5 | 1075 | Max | 31 | 22 | 43 | 25 | 31 | 22 | 42 | 25 | 30% | 322.5 | 0 | 03SQ | ECM | 10" (254mm) | 1095 | 328.5 | 1095 | Max | 38 | 39 | 26 | 33 | 37 | 26
04SQ | ECM | 12" (305mm) | 1950 | 450 | 1500 | Max | 35 | 24 | 45 | 27 | 35 | 24 | 40 | 27 | 30% | 450 | 0 | 04SQ | ECM | 12" (305mm) | 1495 | 448.5 | 1495 | Max | 42 | 42 | 29 | 30 | 39 | 29
05SQ | ECM | 14" (356mm) | 2385.5 | 550.5 | 1835 | Max | 36 | 24 | 47 | 31 | 36 | 24 | 44 | 31 | 30% | 550.5 | 0 | 05SQ | ECM | 14" (356mm) | 2050 | 615 | 2050 | Max | 45 | 46 | 35 | 38 | 39 | 35
06SQ | ECM | 14" (356mm) | 2697.5 | 622.5 | 2075 | Max | 35 | 25 | 48 | 30 | 35 | 25 | 47 | 30 | 30% | 622.5 | 0 | 06SQ | ECM | 14" (356mm) | 2495 | 748.5 | 2495 | Max | 44 | 47 | 30 | 34 | 43 | 30
Inlet SP = 0.75" wg.
Downstream SP = 0.25" wg.
1" Throwaway Filter
VPCF w/ 1/2" matte insulation
Min air valve flow = 30% or minimum valve measurable airflow, whichever is greater
Design cooling valve flow = heating airflow (fan airflow + min valve airflow)
NC calculated using AHRI Standard 885 Appendix E
Maximum airflow not absolute maximum, but maximum with given configuration and static pressure

## SD Background Data (hidden)
| Airflow |  |  | Radiated NC |  | Discharge NC |  | Dimensions (L x W x H) |  |  | Unit Pressure Drop | [11 empty] | 1-Row | [7 empty] | 2-Row | [7 empty] | 3-Row | [7 empty] | 4-Row
Inlet size | max | ddc min | pneumatic | 50% | 80% | 50% | 80% | VCCF | VCEF | VCWF | CFM | VCCF | VCEF | CFM | VCCF | VCEF | CFM | VCCF | VCEF | CFM | VCCF | VCEF | GPM | Delta P | CFM | MBH | APD | CFM | MBH | APD | GPM | Delta P | CFM | MBH | APD | CFM | MBH | APD | GPM | Delta P | CFM | MBH | APD | CFM | MBH | APD | GPM | Delta P | CFM | MBH | APD | CFM | MBH | APD
4 in. round | 225 | 25 | 38 | <15 | 15 | 18 | 26 | 18.25x17x9.5 | 49.25x18.5x11.5 | 24.9x17x9.5 | 112 | 0.01 | 0.01 | 180 | 0.01 | 0.01 | 112 | 0.5 | 14 | 180 | 1 | 18 | 0.5-2.5 | 0.5-8.29 | 112 | 6.46-7.72 | 0.03 | 180 | 7.88-9.9 | 0.05 | 0.5-2.5 | 0.17-3 | 112 | 9.07-11.17 | 0.05 | 180 | 11.46-15.61 | 0.09 | 0.5-2.5 | 0.25-4.3 | 112 | 10.96-13.07 | 0.07 | 180 | 14.14-18.97 | 0.13 | 0.5-2.5 | 0.34-5.61 | 112 | 12.18-14.1 | 0.09 | 180 | 16.01-21.01 | 0.17
5 in. round | 350 | 40 | 63 | <15 | <15 | 17 | 26 | 18.25x17x9.5 | 49.25x18.5x11.5 | 24.9x17x9.5 | 175 | 0.01 | 0.01 | 280 | 0.01 | 0.02 | 175 | 1.5 | 27 | 280 | 2.5 | 28 | 0.5-2.5 | 0.5-8.3 | 175 | 7.79-9.75 | 0.05 | 280 | 9.43-12.52 | 0.09 | 0.5-2.5 | 0.17-3 | 175 | 11.32-15.32 | 0.09 | 280 | 13.5-20.43 | 0.18 | 0.5-2.5 | 0.26-4.31 | 175 | 13.95-18.58 | 0.13 | 280 | 16.79-25.67 | 0.26 | 0.5-2.5 | 0.34-5.63 | 175 | 15.79-20.54 | 0.17 | 280 | 19.14-29.24 | 0.35
6 in. round | 500 | 60 | 73 | <15 | <15 | 17 | 21 | 16.5x17x9.5 | 47.5x18.5x11.5 | 22.4x17x9.5 | 250 | 0.05 | 0.05 | 400 | 0.14 | 0.14 | 250 | 3 | 38 | 400 | 4 | 31 | 0.5-2.5 | 0.5-8.32 | 250 | 9.01-11.78 | 0.12 | 400 | 10.85-15.19 | 0.28 | 0.5-2.5 | 0.18-3.01 | 250 | 13-19.15 | 0.19 | 400 | 14.91-24.62 | 0.43 | 1-2.5 | 0.86-4.33 | 250 | 20.6-23.86 | 0.26 | 400 | 25.57-31.65 | 0.58 | 1-2.5 | 1.13-5.64 | 250 | 23.54-26.99 | 0.33 | 400 | 29.65-36.78 | 0.73
8 in. round | 900 | 105 | 134 | <15 | 19 | 19 | 24 | 16x18x11.5 | 47.5x18.5x11.5 | 21.9x18x11.5 | 450 | 0.02 | 0.03 | 720 | 0.05 | 0.07 | 450 | 6 | 42 | 720 | 7 | 31 | 0.6-2.5 | 0.92-11.08 | 450 | 13.79-18.4 | 0.13 | 720 | 16.4-23.63 | 0.28 | 0.6-2.5 | 0.04-0.47 | 450 | 14.44-27.26 | 0.24 | 720 | 15.61-33.01 | 0.51 | 2.5-12 | 0.54-9.62 | 450 | 35-41.89 | 0.35 | 720 | 43.34-55.78 | 0.74 | 2.5-12 | 0.68-11.78 | 450 | 40.68-47.88 | 0.46 | 720 | 51.36-65.71 | 0.98
10 in. round | 1400 | 165 | 215 | <15 | 20 | <15 | 20 | 17x21x13.5 | 47.5x21.5x13.5 | 22.9x21x13.5 | 700 | 0.01 | 0.01 | 1120 | 0.01 | 0.04 | 700 | 8 | 36 | 1120 | 11 | 31 | 0.9-2.5 | 2.57-15.29 | 700 | 22.06-27.43 | 0.12 | 1120 | 26.44-34.85 | 0.24 | 0.9-2.5 | 0.15-0.98 | 700 | 27.53-41.28 | 0.23 | 1120 | 30.37-49.52 | 0.48 | 2.5-10 | 1.34-17.34 | 700 | 52.4-63.75 | 0.34 | 1120 | 63.78-84.04 | 0.72 | 2.5-10 | 1.81-22.61 | 700 | 60.5-72.99 | 0.46 | 1120 | 74.55-98.94 | 0.97
12 in. round | 2000 | 240 | 300 | <15 | 20 | <15 | 19 | 18x24x15.5 | 47.5x24.5x15.5 | 23.9x24x15.5 | 1000 | 0.01 | 0.02 | 1600 | 0.01 | 0.05 | 1000 | 13 | 41 | 1600 | 16 | 31 | 1.1-5 | 0.76-11.77 | 1000 | 28.66-40.1 | 0.12 | 1600 | 33.63-51.4 | 0.25 | 1.1-5 | 0.08-1.3 | 1000 | 32.63-61.83 | 0.23 | 1600 | 35.22-75.29 | 0.49 | 3.5-14 | 0.85-11.18 | 1000 | 69.78-86.68 | 0.35 | 1600 | 84.03-113.07 | 0.73 | 3.5-14 | 1.02-13.15 | 1000 | 84.04-103.25 | 0.47 | 1600 | 102.69-139.32 | 0.98
14 in. round | 3000 | 320 | 408 | 18 | 23 | 15 | 20 | 19x26x19.5 | 47.5x26.5x19.5 | 24.9x26x19.5 | 1500 | 0.01 | 0.01 | 2400 | 0.01 | 0.01 | 1500 | 20 | 42 | 2400 | 22 | 29 | 2-7 | 1.16-11.24 | 1500 | 45.16-58.62 | 0.13 | 2400 | 53.91-75 | 0.26 | 2-7 | 0.19-1.95 | 1500 | 57.59-91.2 | 0.25 | 2400 | 63.45-110.72 | 0.52 | 5-15 | 1.26-9.93 | 1500 | 107.48-130.05 | 0.37 | 2400 | 129.44-168.24 | 0.78 | 5-15 | 1.49-11.46 | 1500 | 124.5-149.84 | 0.49 | 2400 | 151.59-198.86 | 1.04
16 in. round | 4000 | 420 | 536 | 19 | 25 | 17 | 23 | 20x30x19.5 | 47.5x30.5x19.5 | 25.9x30x19.5 | 2000 | 0.01 | 0.01 | 3200 | 0.01 | 0.02 | 2000 | 28 | 44 | 3200 | 30 | 30 | 2.3-7.5 | 1.65-13.99 | 2000 | 57.08-74.16 | 0.15 | 3200 | 67.87-94.61 | 0.31 | 2.3-7.5 | 0.26-2.35 | 2000 | 72.94-114.54 | 0.29 | 3200 | 79.93-137.37 | 0.61 | 5-17 | 1.35-13.34 | 2000 | 130.77-166.98 | 0.43 | 3200 | 153.8-213.72 | 0.91 | 5-17 | 1.61-15.5 | 2000 | 151.23-193.3 | 0.57 | 3200 | 178.8-253.36 | 1.22
16 in. x 24 in. rect | 8000 | 800 | 1096 | 26 | 33 | 23 | 29 | 23x34x19.5 | 47.5x34.5x19.5 | 28.9x34x19.5 | 4000 | 0.01 | 0.15 | 6400 | 0.01 | 0.42 | 4000 | 46 | 36 | 6400 | 46 | 23 | 4-7 | 4.91-13.49 | 4000 | 96.16-111.02 | 0.41 | 5100 | 106-124.93 | 0.62 | 4-7 | 0.9-2.53 | 4000 | 124.75-156.6 | 0.74 | 5100 | 131.12-167.76 | 1.12 | 5-17 | 1.45-14.1 | 4000 | 174.69-254.01 | 1.08 | 5100 | 184.83-281.03 | 1.62 | 5-17 | 1.75-16.54 | 4000 | 201.24-301.32 | 1.41 | 5100 | 212.51-336.12 | 2.11
VCCF
VCEF
VCWF

## VCWF Data (hidden)
[5 empty] | Tag | Inlet Size | CFM | GPM | WPD | MBH | APD | Key | 1R
4 | - | 1R | - | 50L | 4-1R-50L | 4" | 112 | 0.5 | 0.5 | 6.46 | 0.03 | 1R = 3-Row HW Coil | GPM | WPD1 | CFM1 | MBH1 | APD1 | CFM2 | MBH2 | APD2
5 | - | 1R | - | 50L | 5-1R-50L | 5" | 175 | 0.5 | 0.5 | 7.79 | 0.05 | 2R = 4-Row HW Coil | 0.5-2.5 | 0.5-8.29 | 112 | 6.46-7.72 | 0.03 | 180 | 7.88-9.9 | 0.05
6 | - | 1R | - | 50L | 6-1R-50L | 6" | 250 | 0.5 | 0.5 | 9.01 | 0.12 | 3R = 3-Row HW Coil | 0.5-2.5 | 0.5-8.3 | 175 | 7.79-9.75 | 0.05 | 280 | 9.43-12.52 | 0.09
8 | - | 1R | - | 50L | 8-1R-50L | 8" | 450 | 0.6 | 0.92 | 13.79 | 0.13 | 4R = 4-Row HW Coil | 0.5-2.5 | 0.5-8.32 | 250 | 9.01-11.78 | 0.12 | 400 | 10.85-15.19 | 0.28
10 | - | 1R | - | 50L | 10-1R-50L | 10" | 700 | 0.9 | 2.57 | 22.06 | 0.12 | 50 = 50% max aiflow | 0.6-2.5 | 0.92-11.08 | 450 | 13.79-18.4 | 0.13 | 720 | 16.4-23.63 | 0.28
12 | - | 1R | - | 50L | 12-1R-50L | 12" | 1000 | 1.1 | 0.76 | 28.66 | 0.12 | 80 = 80% max airflow | 0.9-2.5 | 2.57-15.29 | 700 | 22.06-27.43 | 0.12 | 1120 | 26.44-34.85 | 0.24
14 | - | 1R | - | 50L | 14-1R-50L | 14" | 1500 | 2 | 1.16 | 45.16 | 0.13 | L = Low GPM | 1.1-5 | 0.76-11.77 | 1000 | 28.66-40.1 | 0.12 | 1600 | 33.63-51.4 | 0.25
16 | - | 1R | - | 50L | 16-1R-50L | 16" | 2000 | 2.3 | 1.65 | 57.08 | 0.15 | H = High GPM | 2-7 | 1.16-11.24 | 1500 | 45.16-58.62 | 0.13 | 2400 | 53.91-75 | 0.26
24 | - | 1R | - | 50L | 24-1R-50L | 16"x24" | 4000 | 4 | 4.91 | 96.16 | 0.41 |  | 2.3-7.5 | 1.65-13.99 | 2000 | 57.08-74.16 | 0.15 | 3200 | 67.87-94.61 | 0.31
4 | - | 1R | - | 50H | 4-1R-50H | 4" | 112 | 2.5 | 8.29 | 7.72 | 0.03 | 180F EWT | 4-7 | 4.91-13.49 | 4000 | 96.16-111.02 | 0.41 | 5100 | 106-124.93 | 0.62
5 | - | 1R | - | 50H | 5-1R-50H | 5" | 175 | 2.5 | 8.3 | 9.75 | 0.05
6 | - | 1R | - | 50H | 6-1R-50H | 6" | 250 | 2.5 | 8.32 | 11.78 | 0.12 |  | 2R
8 | - | 1R | - | 50H | 8-1R-50H | 8" | 450 | 2.5 | 11.08 | 18.4 | 0.13 |  | GPM | WPD1 | CFM1 | MBH1 | APD1 | CFM2 | MBH2 | APD2
10 | - | 1R | - | 50H | 10-1R-50H | 10" | 700 | 2.5 | 15.29 | 27.43 | 0.12 |  | 0.5-2.5 | 0.17-3 | 112 | 9.07-11.17 | 0.05 | 180 | 11.46-15.61 | 0.09
12 | - | 1R | - | 50H | 12-1R-50H | 12" | 1000 | 5 | 11.77 | 40.1 | 0.12 |  | 0.5-2.5 | 0.17-3 | 175 | 11.32-15.32 | 0.09 | 280 | 13.5-20.43 | 0.18
14 | - | 1R | - | 50H | 14-1R-50H | 14" | 1500 | 7 | 11.24 | 58.62 | 0.13 |  | 0.5-2.5 | 0.18-3.01 | 250 | 13-19.15 | 0.19 | 400 | 14.91-24.62 | 0.43
16 | - | 1R | - | 50H | 16-1R-50H | 16" | 2000 | 7.5 | 13.99 | 74.16 | 0.15 |  | 0.6-2.5 | 0.04-0.47 | 450 | 14.44-27.26 | 0.24 | 720 | 15.61-33.01 | 0.51
24 | - | 1R | - | 50H | 24-1R-50H | 16"x24" | 4000 | 7 | 13.49 | 111.02 | 0.41 |  | 0.9-2.5 | 0.15-0.98 | 700 | 27.53-41.28 | 0.23 | 1120 | 30.37-49.52 | 0.48
4 | - | 2R | - | 50L | 4-2R-50L | 4" | 112 | 0.5 | 0.17 | 9.07 | 0.05 |  | 1.1-5 | 0.08-1.3 | 1000 | 32.63-61.83 | 0.23 | 1600 | 35.22-75.29 | 0.49
5 | - | 2R | - | 50L | 5-2R-50L | 5" | 175 | 0.5 | 0.17 | 11.32 | 0.09 |  | 2-7 | 0.19-1.95 | 1500 | 57.59-91.2 | 0.25 | 2400 | 63.45-110.72 | 0.52
6 | - | 2R | - | 50L | 6-2R-50L | 6" | 250 | 0.5 | 0.18 | 13 | 0.19 |  | 2.3-7.5 | 0.26-2.35 | 2000 | 72.94-114.54 | 0.29 | 3200 | 79.93-137.37 | 0.61
8 | - | 2R | - | 50L | 8-2R-50L | 8" | 450 | 0.6 | 0.04 | 14.44 | 0.24 |  | 4-7 | 0.9-2.53 | 4000 | 124.75-156.6 | 0.74 | 5100 | 131.12-167.76 | 1.12
10 | - | 2R | - | 50L | 10-2R-50L | 10" | 700 | 0.9 | 0.15 | 27.53 | 0.23
12 | - | 2R | - | 50L | 12-2R-50L | 12" | 1000 | 1.1 | 0.08 | 32.63 | 0.23 |  | 3R
14 | - | 2R | - | 50L | 14-2R-50L | 14" | 1500 | 2 | 0.19 | 57.59 | 0.25 |  | GPM | WPD1 | CFM1 | MBH1 | APD1 | CFM2 | MBH2 | APD2
16 | - | 2R | - | 50L | 16-2R-50L | 16" | 2000 | 2.3 | 0.26 | 72.94 | 0.29 |  | 0.5-2.5 | 0.25-4.3 | 112 | 10.96-13.07 | 0.07 | 180 | 14.14-18.97 | 0.13
24 | - | 2R | - | 50L | 24-2R-50L | 16"x24" | 4000 | 4 | 0.9 | 124.75 | 0.74 |  | 0.5-2.5 | 0.26-4.31 | 175 | 13.95-18.58 | 0.13 | 280 | 16.79-25.67 | 0.26
4 | - | 2R | - | 50H | 4-2R-50H | 4" | 112 | 2.5 | 3 | 11.17 | 0.05 |  | 1-2.5 | 0.86-4.33 | 250 | 20.6-23.86 | 0.26 | 400 | 25.57-31.65 | 0.58
5 | - | 2R | - | 50H | 5-2R-50H | 5" | 175 | 2.5 | 3 | 15.32 | 0.09 |  | 2.5-12 | 0.54-9.62 | 450 | 35-41.89 | 0.35 | 720 | 43.34-55.78 | 0.74
6 | - | 2R | - | 50H | 6-2R-50H | 6" | 250 | 2.5 | 3.01 | 19.15 | 0.19 |  | 2.5-10 | 1.34-17.34 | 700 | 52.4-63.75 | 0.34 | 1120 | 63.78-84.04 | 0.72
8 | - | 2R | - | 50H | 8-2R-50H | 8" | 450 | 2.5 | 0.47 | 27.26 | 0.24 |  | 3.5-14 | 0.85-11.18 | 1000 | 69.78-86.68 | 0.35 | 1600 | 84.03-113.07 | 0.73
10 | - | 2R | - | 50H | 10-2R-50H | 10" | 700 | 2.5 | 0.98 | 41.28 | 0.23 |  | 5-15 | 1.26-9.93 | 1500 | 107.48-130.05 | 0.37 | 2400 | 129.44-168.24 | 0.78
12 | - | 2R | - | 50H | 12-2R-50H | 12" | 1000 | 5 | 1.3 | 61.83 | 0.23 |  | 5-17 | 1.35-13.34 | 2000 | 130.77-166.98 | 0.43 | 3200 | 153.8-213.72 | 0.91
14 | - | 2R | - | 50H | 14-2R-50H | 14" | 1500 | 7 | 1.95 | 91.2 | 0.25 |  | 5-17 | 1.45-14.1 | 4000 | 174.69-254.01 | 1.08 | 5100 | 184.83-281.03 | 1.62
16 | - | 2R | - | 50H | 16-2R-50H | 16" | 2000 | 7.5 | 2.35 | 114.54 | 0.29
24 | - | 2R | - | 50H | 24-2R-50H | 16"x24" | 4000 | 7 | 2.53 | 156.6 | 0.74 |  | 4R
4 | - | 1R | - | 80L | 4-1R-80L | 4" | 180 | 0.5 | 0.5 | 7.88 | 0.05 |  | GPM | WPD1 | CFM1 | MBH1 | APD1 | CFM2 | MBH2 | APD2
5 | - | 1R | - | 80L | 5-1R-80L | 5" | 280 | 0.5 | 0.5 | 9.43 | 0.09 |  | 0.5-2.5 | 0.34-5.61 | 112 | 12.18-14.1 | 0.09 | 180 | 16.01-21.01 | 0.17
6 | - | 1R | - | 80L | 6-1R-80L | 6" | 400 | 0.5 | 0.5 | 10.85 | 0.28 |  | 0.5-2.5 | 0.34-5.63 | 175 | 15.79-20.54 | 0.17 | 280 | 19.14-29.24 | 0.35
8 | - | 1R | - | 80L | 8-1R-80L | 8" | 720 | 0.6 | 0.93 | 16.4 | 0.28 |  | 1-2.5 | 1.13-5.64 | 250 | 23.54-26.99 | 0.33 | 400 | 29.65-36.78 | 0.73
10 | - | 1R | - | 80L | 10-1R-80L | 10" | 1120 | 0.9 | 2.6 | 26.44 | 0.24 |  | 2.5-12 | 0.68-11.78 | 450 | 40.68-47.88 | 0.46 | 720 | 51.36-65.71 | 0.98
12 | - | 1R | - | 80L | 12-1R-80L | 12" | 1600 | 1.1 | 0.77 | 33.63 | 0.25 |  | 2.5-10 | 1.81-22.61 | 700 | 60.5-72.99 | 0.46 | 1120 | 74.55-98.94 | 0.97
14 | - | 1R | - | 80L | 14-1R-80L | 14" | 2400 | 2 | 1.17 | 53.91 | 0.26 |  | 3.5-14 | 1.02-13.15 | 1000 | 84.04-103.25 | 0.47 | 1600 | 102.69-139.32 | 0.98
16 | - | 1R | - | 80L | 16-1R-80L | 16" | 3200 | 2.3 | 1.66 | 67.87 | 0.31 |  | 5-15 | 1.49-11.46 | 1500 | 124.5-149.84 | 0.49 | 2400 | 151.59-198.86 | 1.04
24 | - | 1R | - | 80L | 24-1R-80L | 16"x24" | 5100 | 4 | 4.93 | 106 | 0.62 |  | 5-17 | 1.61-15.5 | 2000 | 151.23-193.3 | 0.57 | 3200 | 178.8-253.36 | 1.22
4 | - | 1R | - | 50H | 4-1R-50H | 4" | 180 | 2.5 | 8.3 | 9.9 | 0.05 |  | 5-17 | 1.75-16.54 | 4000 | 201.24-301.32 | 1.41 | 5100 | 212.51-336.12 | 2.11
5 | - | 1R | - | 50H | 5-1R-50H | 5" | 280 | 2.5 | 8.32 | 12.52 | 0.09
6 | - | 1R | - | 50H | 6-1R-50H | 6" | 400 | 2.5 | 8.34 | 15.19 | 0.28
8 | - | 1R | - | 50H | 8-1R-50H | 8" | 720 | 2.5 | 11.12 | 23.63 | 0.28
10 | - | 1R | - | 50H | 10-1R-50H | 10" | 1120 | 2.5 | 15.37 | 34.85 | 0.24
12 | - | 1R | - | 50H | 12-1R-50H | 12" | 1600 | 5 | 11.8 | 51.4 | 0.25
14 | - | 1R | - | 50H | 14-1R-50H | 14" | 2400 | 7 | 11.27 | 75 | 0.26
16 | - | 1R | - | 50H | 16-1R-50H | 16" | 3200 | 7.5 | 14.04 | 94.61 | 0.31
24 | - | 1R | - | 50H | 24-1R-50H | 16"x24" | 5100 | 7 | 13.53 | 124.93 | 0.62
4 | - | 2R | - | 80L | 4-2R-80L | 4" | 180 | 0.5 | 0.17 | 11.46 | 0.09
5 | - | 2R | - | 80L | 5-2R-80L | 5" | 280 | 0.5 | 0.18 | 13.5 | 0.18
6 | - | 2R | - | 80L | 6-2R-80L | 6" | 400 | 0.5 | 0.18 | 14.91 | 0.43
8 | - | 2R | - | 80L | 8-2R-80L | 8" | 720 | 0.6 | 0.04 | 15.61 | 0.51
10 | - | 2R | - | 80L | 10-2R-80L | 10" | 1120 | 0.9 | 0.15 | 30.37 | 0.48
12 | - | 2R | - | 80L | 12-2R-80L | 12" | 1600 | 1.1 | 0.08 | 35.22 | 0.49
14 | - | 2R | - | 80L | 14-2R-80L | 14" | 2400 | 2 | 0.19 | 63.45 | 0.52
16 | - | 2R | - | 80L | 16-2R-80L | 16" | 3200 | 2.3 | 0.26 | 79.93 | 0.61
24 | - | 2R | - | 80L | 24-2R-80L | 16"x24" | 5100 | 4 | 0.9 | 131.12 | 1.12
4 | - | 2R | - | 50H | 4-2R-50H | 4" | 180 | 2.5 | 3 | 15.61 | 0.09
5 | - | 2R | - | 50H | 5-2R-50H | 5" | 280 | 2.5 | 3.01 | 20.43 | 0.18
6 | - | 2R | - | 50H | 6-2R-50H | 6" | 400 | 2.5 | 3.02 | 24.62 | 0.43
8 | - | 2R | - | 50H | 8-2R-50H | 8" | 720 | 2.5 | 0.47 | 33.01 | 0.51
10 | - | 2R | - | 50H | 10-2R-50H | 10" | 1120 | 2.5 | 0.98 | 49.52 | 0.48
12 | - | 2R | - | 50H | 12-2R-50H | 12" | 1600 | 5 | 1.31 | 75.29 | 0.49
14 | - | 2R | - | 50H | 14-2R-50H | 14" | 2400 | 7 | 1.96 | 110.72 | 0.52
16 | - | 2R | - | 50H | 16-2R-50H | 16" | 3200 | 7.5 | 2.35 | 137.37 | 0.61
24 | - | 2R | - | 50H | 24-2R-50H | 16"x24" | 5100 | 7 | 2.54 | 167.76 | 1.12
4 | - | 3R | - | 50L | 4-3R-50L | 4" | 112 | 0.5 | 0.25 | 10.96 | 0.07
5 | - | 3R | - | 50L | 5-3R-50L | 5" | 175 | 0.5 | 0.26 | 13.95 | 0.13
6 | - | 3R | - | 50L | 6-3R-50L | 6" | 250 | 1 | 0.86 | 20.6 | 0.26
8 | - | 3R | - | 50L | 8-3R-50L | 8" | 450 | 2.5 | 0.54 | 35 | 0.35
10 | - | 3R | - | 50L | 10-3R-50L | 10" | 700 | 2.5 | 1.34 | 52.4 | 0.34
12 | - | 3R | - | 50L | 12-3R-50L | 12" | 1000 | 3.5 | 0.85 | 69.78 | 0.35
14 | - | 3R | - | 50L | 14-3R-50L | 14" | 1500 | 5 | 1.26 | 107.48 | 0.37
16 | - | 3R | - | 50L | 16-3R-50L | 16" | 2000 | 5 | 1.35 | 130.77 | 0.43
24 | - | 3R | - | 50L | 24-3R-50L | 16"x24" | 4000 | 5 | 1.45 | 174.69 | 1.08
4 | - | 3R | - | 50H | 4-3R-50H | 4" | 112 | 2.5 | 4.3 | 13.07 | 0.07
5 | - | 3R | - | 50H | 5-3R-50H | 5" | 175 | 2.5 | 4.31 | 18.58 | 0.13
6 | - | 3R | - | 50H | 6-3R-50H | 6" | 250 | 2.5 | 4.33 | 23.86 | 0.26
8 | - | 3R | - | 50H | 8-3R-50H | 8" | 450 | 12 | 9.62 | 41.89 | 0.35
10 | - | 3R | - | 50H | 10-3R-50H | 10" | 700 | 10 | 17.34 | 63.75 | 0.34
12 | - | 3R | - | 50H | 12-3R-50H | 12" | 1000 | 14 | 11.18 | 86.68 | 0.35
14 | - | 3R | - | 50H | 14-3R-50H | 14" | 1500 | 15 | 9.93 | 130.05 | 0.37
16 | - | 3R | - | 50H | 16-3R-50H | 16" | 2000 | 17 | 13.34 | 166.98 | 0.43
24 | - | 3R | - | 50H | 24-3R-50H | 16"x24" | 4000 | 17 | 14.1 | 254.01 | 1.08
4 | - | 4R | - | 50L | 4-4R-50L | 4" | 112 | 0.5 | 0.34 | 12.18 | 0.09
5 | - | 4R | - | 50L | 5-4R-50L | 5" | 175 | 0.5 | 0.34 | 15.79 | 0.17
6 | - | 4R | - | 50L | 6-4R-50L | 6" | 250 | 1 | 1.13 | 23.54 | 0.33
8 | - | 4R | - | 50L | 8-4R-50L | 8" | 450 | 2.5 | 0.68 | 40.68 | 0.46
10 | - | 4R | - | 50L | 10-4R-50L | 10" | 700 | 2.5 | 1.81 | 60.5 | 0.46
12 | - | 4R | - | 50L | 12-4R-50L | 12" | 1000 | 3.5 | 1.02 | 84.04 | 0.47
14 | - | 4R | - | 50L | 14-4R-50L | 14" | 1500 | 5 | 1.49 | 124.5 | 0.49
16 | - | 4R | - | 50L | 16-4R-50L | 16" | 2000 | 5 | 1.61 | 151.23 | 0.57
24 | - | 4R | - | 50L | 24-4R-50L | 16"x24" | 4000 | 5 | 1.75 | 201.24 | 1.41
4 | - | 4R | - | 50H | 4-4R-50H | 4" | 112 | 2.5 | 5.61 | 14.1 | 0.09
5 | - | 4R | - | 50H | 5-4R-50H | 5" | 175 | 2.5 | 5.63 | 20.54 | 0.17
6 | - | 4R | - | 50H | 6-4R-50H | 6" | 250 | 2.5 | 5.64 | 26.99 | 0.33
8 | - | 4R | - | 50H | 8-4R-50H | 8" | 450 | 12 | 11.78 | 47.88 | 0.46
10 | - | 4R | - | 50H | 10-4R-50H | 10" | 700 | 10 | 22.61 | 72.99 | 0.46
12 | - | 4R | - | 50H | 12-4R-50H | 12" | 1000 | 14 | 13.15 | 103.25 | 0.47
14 | - | 4R | - | 50H | 14-4R-50H | 14" | 1500 | 15 | 11.46 | 149.84 | 0.49
16 | - | 4R | - | 50H | 16-4R-50H | 16" | 2000 | 17 | 15.5 | 193.3 | 0.57
24 | - | 4R | - | 50H | 24-4R-50H | 16"x24" | 4000 | 17 | 16.54 | 301.32 | 1.41
4 | - | 3R | - | 80L | 4-3R-80L | 4" | 180 | 0.5 | 0.26 | 14.14 | 0.13
5 | - | 3R | - | 80L | 5-3R-80L | 5" | 280 | 0.5 | 0.26 | 16.79 | 0.26
6 | - | 3R | - | 80L | 6-3R-80L | 6" | 400 | 1 | 0.86 | 25.57 | 0.58
8 | - | 3R | - | 80L | 8-3R-80L | 8" | 720 | 2.5 | 0.54 | 43.34 | 0.74
10 | - | 3R | - | 80L | 10-3R-80L | 10" | 1120 | 2.5 | 1.35 | 63.78 | 0.72
12 | - | 3R | - | 80L | 12-3R-80L | 12" | 1600 | 3.5 | 0.85 | 84.03 | 0.73
14 | - | 3R | - | 80L | 14-3R-80L | 14" | 2400 | 5 | 1.26 | 129.44 | 0.78
16 | - | 3R | - | 80L | 16-3R-80L | 16" | 3200 | 5 | 1.36 | 153.8 | 0.91
24 | - | 3R | - | 80L | 24-3R-80L | 16"x24" | 5100 | 5 | 1.45 | 184.83 | 1.62
4 | - | 3R | - | 50H | 4-3R-50H | 4" | 180 | 2.5 | 4.32 | 18.97 | 0.13
5 | - | 3R | - | 50H | 5-3R-50H | 5" | 280 | 2.5 | 4.33 | 25.67 | 0.26
6 | - | 3R | - | 50H | 6-3R-50H | 6" | 400 | 2.5 | 4.34 | 31.65 | 0.58
8 | - | 3R | - | 50H | 8-3R-50H | 8" | 720 | 12 | 9.63 | 55.78 | 0.74
10 | - | 3R | - | 50H | 10-3R-50H | 10" | 1120 | 10 | 17.36 | 84.04 | 0.72
12 | - | 3R | - | 50H | 12-3R-50H | 12" | 1600 | 14 | 11.19 | 113.07 | 0.73
14 | - | 3R | - | 50H | 14-3R-50H | 14" | 2400 | 15 | 9.94 | 168.24 | 0.78
16 | - | 3R | - | 50H | 16-3R-50H | 16" | 3200 | 17 | 13.35 | 213.72 | 0.91
24 | - | 3R | - | 50H | 24-3R-50H | 16"x24" | 5100 | 17 | 14.12 | 281.03 | 1.62
4 | - | 4R | - | 80L | 4-4R-80L | 4" | 180 | 0.5 | 0.34 | 16.01 | 0.17
5 | - | 4R | - | 80L | 5-4R-80L | 5" | 280 | 0.5 | 0.34 | 19.14 | 0.35
6 | - | 4R | - | 80L | 6-4R-80L | 6" | 400 | 1 | 1.14 | 29.65 | 0.73
8 | - | 4R | - | 80L | 8-4R-80L | 8" | 720 | 2.5 | 0.69 | 51.36 | 0.98
10 | - | 4R | - | 80L | 10-4R-80L | 10" | 1120 | 2.5 | 1.83 | 74.55 | 0.97
12 | - | 4R | - | 80L | 12-4R-80L | 12" | 1600 | 3.5 | 1.03 | 102.69 | 0.98
14 | - | 4R | - | 80L | 14-4R-80L | 14" | 2400 | 5 | 1.5 | 151.59 | 1.04
16 | - | 4R | - | 80L | 16-4R-80L | 16" | 3200 | 5 | 1.62 | 178.8 | 1.22
24 | - | 4R | - | 80L | 24-4R-80L | 16"x24" | 5100 | 5 | 1.76 | 212.51 | 2.11
4 | - | 4R | - | 50H | 4-4R-50H | 4" | 180 | 2.5 | 5.63 | 21.01 | 0.17
5 | - | 4R | - | 50H | 5-4R-50H | 5" | 280 | 2.5 | 5.65 | 29.24 | 0.35
6 | - | 4R | - | 50H | 6-4R-50H | 6" | 400 | 2.5 | 5.67 | 36.78 | 0.73
8 | - | 4R | - | 50H | 8-4R-50H | 8" | 720 | 12 | 11.8 | 65.71 | 0.98
10 | - | 4R | - | 50H | 10-4R-50H | 10" | 1120 | 10 | 22.65 | 98.94 | 0.97
12 | - | 4R | - | 50H | 12-4R-50H | 12" | 1600 | 14 | 13.18 | 139.32 | 0.98
14 | - | 4R | - | 50H | 14-4R-50H | 14" | 2400 | 15 | 11.48 | 198.86 | 1.04
16 | - | 4R | - | 50H | 16-4R-50H | 16" | 3200 | 17 | 15.53 | 253.36 | 1.22
24 | - | 4R | - | 50H | 24-4R-50H | 16"x24" | 5100 | 17 | 16.56 | 336.12 | 2.11

## SD TOPSS Source Data (hidden)
Variable Air Volume Single Duct Terminal Units
Schedule
Unit Tags | Quantity
|  | Unit model | Primary inlet | Design cooling airflow | Min cooling airflow | APD @ cooling airflow | Valve heating airflow | Unit Insulation | Operating weight | Primary EDB | Fluid type | Heating ent fluid temp | Heating flow rate | Heating delta T | Coil fluid PD | Coil heating capacity | Hot water coil | Discharge valve - 125 Hz | Discharge valve - 250 Hz | Discharge valve - 500 Hz | Discharge valve - 1 kHz | Discharge valve - 2 kHz | Discharge valve - 4 kHz | Discharge valve - NC | Radiated valve - 125 Hz | Radiated valve - 250 Hz | Radiated valve - 500 Hz | Radiated valve - 1 kHz | Radiated valve - 2 kHz | Radiated valve - 4 kHz | Radiated valve - NC | Max inlet SP | Discharge transfer function | Radiated transfer function
|  |  |  | cfm | cfm | in H2O | cfm |  | lb | F |  | F | gpm | F | ft H2O | MBh |  | dB | dB | dB | dB | dB | dB |  | dB | dB | dB | dB | dB | dB |  | in H2O
4-3R-50L | 1 | VCWF (Hot Water Heating) | 4" (102mm) | 112 | 112 | 0.04 | 112 | 1/2" matte | 22 | 55 | Water | 180 | 0.5 | 40.74 | 0.25 | 10.19 | 3 Row hot water coil
5-3R-50L | 1 | VCWF (Hot Water Heating) | 5" (127mm) | 175 | 175 | 0.09 | 175 | 1/2" matte | 22 | 55 | Water | 180 | 0.5 | 51.63 | 0.25 | 12.91 | 3 Row hot water coil
6-3R-50L | 1 | VCWF (Hot Water Heating) | 6" (152mm) | 250 | 250 | 0.18 | 250 | 1/2" matte | 22 | 55 | Water | 180 | 1 | 37.48 | 0.84 | 18.75 | 3 Row hot water coil
8-3R-50L | 1 | VCWF (Hot Water Heating) | 8" (203mm) | 450 | 450 | 0.29 | 450 | 1/2" matte | 24 | 55 | Water | 180 | 2.5 | 25.26 | 0.53 | 31.61 | 3 Row hot water coil
10-3R-50L | 1 | VCWF (Hot Water Heating) | 10" (254mm) | 700 | 700 | 0.3 | 700 | 1/2" matte | 32 | 55 | Water | 180 | 2.5 | 38.08 | 1.32 | 47.62 | 3 Row hot water coil
12-3R-50L | 1 | VCWF (Hot Water Heating) | 12" (305mm) | 1000 | 1000 | 0.32 | 1000 | 1/2" matte | 41 | 55 | Water | 180 | 3.5 | 36.37 | 0.83 | 63.68 | 3 Row hot water coil
14-3R-50L | 1 | VCWF (Hot Water Heating) | 14" (356mm) | 1500 | 1500 | 0.34 | 1500 | 1/2" matte | 51 | 55 | Water | 180 | 5 | 39.33 | 1.25 | 98.35 | 3 Row hot water coil
16-3R-50L | 1 | VCWF (Hot Water Heating) | 16" (406mm) | 2000 | 2000 | 0.39 | 2000 | 1/2" matte | 56 | 55 | Water | 180 | 5 | 48.06 | 1.34 | 120.14 | 3 Row hot water coil
24-3R-50L | 1 | VCWF (Hot Water Heating) | 24" x 16" (610x406mm) | 4000 | 4000 | 0.96 | 4000 | 1/2" matte | 76 | 55 | Water | 180 | 5 | 64.71 | 1.44 | 161.65 | 3 Row hot water coil
4-3R-50R | 1 | VCWF (Hot Water Heating) | 4" (102mm) | 112 | 112 | 0.04 | 112 | 1/2" matte | 22 | 55 | Water | 180 | 2.5 | 9.74 | 4.21 | 12.2 | 3 Row hot water coil
5-3R-50R | 1 | VCWF (Hot Water Heating) | 5" (127mm) | 175 | 175 | 0.09 | 175 | 1/2" matte | 22 | 55 | Water | 180 | 2.5 | 13.6 | 4.22 | 17.03 | 3 Row hot water coil
6-3R-50R | 1 | VCWF (Hot Water Heating) | 6" (152mm) | 250 | 250 | 0.18 | 250 | 1/2" matte | 22 | 55 | Water | 180 | 2.5 | 17.24 | 4.23 | 21.58 | 3 Row hot water coil
8-3R-50R | 1 | VCWF (Hot Water Heating) | 8" (203mm) | 450 | 450 | 0.29 | 450 | 1/2" matte | 24 | 55 | Water | 180 | 12 | 6.24 | 9.47 | 37.49 | 3 Row hot water coil
10-3R-50R | 1 | VCWF (Hot Water Heating) | 10" (254mm) | 700 | 700 | 0.3 | 700 | 1/2" matte | 32 | 55 | Water | 180 | 10 | 11.44 | 17.13 | 57.28 | 3 Row hot water coil
12-3R-50R | 1 | VCWF (Hot Water Heating) | 12" (305mm) | 1000 | 1000 | 0.32 | 1000 | 1/2" matte | 41 | 55 | Water | 180 | 14 | 11.12 | 11.07 | 78.01 | 3 Row hot water coil
14-3R-50R | 1 | VCWF (Hot Water Heating) | 14" (356mm) | 1500 | 1500 | 0.34 | 1500 | 1/2" matte | 51 | 55 | Water | 180 | 15 | 15.65 | 9.85 | 117.58 | 3 Row hot water coil
16-3R-50R | 1 | VCWF (Hot Water Heating) | 16" (406mm) | 2000 | 2000 | 0.39 | 2000 | 1/2" matte | 56 | 55 | Water | 180 | 17 | 17.71 | 13.24 | 150.76 | 3 Row hot water coil
24-3R-50R | 1 | VCWF (Hot Water Heating) | 24" x 16" (610x406mm) | 4000 | 4000 | 0.96 | 4000 | 1/2" matte | 76 | 55 | Water | 180 | 17 | 26.71 | 14 | 227.24 | 3 Row hot water coil
4-4R-50L | 1 | VCWF (Hot Water Heating) | 4" (102mm) | 112 | 112 | 0.05 | 112 | 1/2" matte | 24 | 55 | Water | 180 | 0.5 | 45.93 | 0.33 | 11.48 | 4 Row hot water coil
5-4R-50L | 1 | VCWF (Hot Water Heating) | 5" (127mm) | 175 | 175 | 0.13 | 175 | 1/2" matte | 24 | 55 | Water | 180 | 0.5 | 59.13 | 0.33 | 14.78 | 4 Row hot water coil
6-4R-50L | 1 | VCWF (Hot Water Heating) | 6" (152mm) | 250 | 250 | 0.24 | 250 | 1/2" matte | 24 | 55 | Water | 180 | 1 | 43.44 | 1.1 | 21.72 | 4 Row hot water coil
8-4R-50L | 1 | VCWF (Hot Water Heating) | 8" (203mm) | 450 | 450 | 0.38 | 450 | 1/2" matte | 26 | 55 | Water | 180 | 2.5 | 29.78 | 0.67 | 37.25 | 4 Row hot water coil
10-4R-50L | 1 | VCWF (Hot Water Heating) | 10" (254mm) | 700 | 700 | 0.4 | 700 | 1/2" matte | 36 | 55 | Water | 180 | 2.5 | 44.55 | 1.78 | 55.7 | 4 Row hot water coil
12-4R-50L | 1 | VCWF (Hot Water Heating) | 12" (305mm) | 1000 | 1000 | 0.41 | 1000 | 1/2" matte | 45 | 55 | Water | 180 | 3.5 | 44.45 | 1.01 | 77.8 | 4 Row hot water coil
14-4R-50L | 1 | VCWF (Hot Water Heating) | 14" (356mm) | 1500 | 1500 | 0.43 | 1500 | 1/2" matte | 55 | 55 | Water | 180 | 5 | 46.1 | 1.47 | 115.26 | 4 Row hot water coil
16-4R-50L | 1 | VCWF (Hot Water Heating) | 16" (406mm) | 2000 | 2000 | 0.52 | 2000 | 1/2" matte | 61 | 55 | Water | 180 | 5 | 56.2 | 1.59 | 140.46 | 4 Row hot water coil
24-4R-50L | 1 | VCWF (Hot Water Heating) | 24" x 16" (610x406mm) | 4000 | 4000 | 1.27 | 4000 | 1/2" matte | 82 | 55 | Water | 180 | 5 | 75.39 | 1.73 | 188.26 | 4 Row hot water coil
4-4R-50R | 1 | VCWF (Hot Water Heating) | 4" (102mm) | 112 | 112 | 0.05 | 112 | 1/2" matte | 24 | 55 | Water | 180 | 2.5 | 10.71 | 5.49 | 13.42 | 4 Row hot water coil
5-4R-50R | 1 | VCWF (Hot Water Heating) | 5" (127mm) | 175 | 175 | 0.13 | 175 | 1/2" matte | 24 | 55 | Water | 180 | 2.5 | 15.36 | 5.5 | 19.23 | 4 Row hot water coil
6-4R-50R | 1 | VCWF (Hot Water Heating) | 6" (152mm) | 250 | 250 | 0.24 | 250 | 1/2" matte | 24 | 55 | Water | 180 | 2.5 | 19.88 | 5.52 | 24.88 | 4 Row hot water coil
8-4R-50R | 1 | VCWF (Hot Water Heating) | 8" (203mm) | 450 | 450 | 0.38 | 450 | 1/2" matte | 26 | 55 | Water | 180 | 12 | 7.28 | 11.59 | 43.75 | 4 Row hot water coil
10-4R-50R | 1 | VCWF (Hot Water Heating) | 10" (254mm) | 700 | 700 | 0.4 | 700 | 1/2" matte | 36 | 55 | Water | 180 | 10 | 13.35 | 22.3 | 66.84 | 4 Row hot water coil
12-4R-50R | 1 | VCWF (Hot Water Heating) | 12" (305mm) | 1000 | 1000 | 0.41 | 1000 | 1/2" matte | 45 | 55 | Water | 180 | 14 | 13.54 | 13.01 | 94.96 | 4 Row hot water coil
14-4R-50R | 1 | VCWF (Hot Water Heating) | 14" (356mm) | 1500 | 1500 | 0.43 | 1500 | 1/2" matte | 55 | 55 | Water | 180 | 15 | 18.34 | 11.36 | 137.71 | 4 Row hot water coil
16-4R-50R | 1 | VCWF (Hot Water Heating) | 16" (406mm) | 2000 | 2000 | 0.52 | 2000 | 1/2" matte | 61 | 55 | Water | 180 | 17 | 20.83 | 15.37 | 177.27 | 4 Row hot water coil
24-4R-50R | 1 | VCWF (Hot Water Heating) | 24" x 16" (610x406mm) | 4000 | 4000 | 1.27 | 4000 | 1/2" matte | 82 | 55 | Water | 180 | 17 | 32.08 | 16.4 | 272.92 | 4 Row hot water coil
4-3R-80L | 1 | VCWF (Hot Water Heating) | 4" (102mm) | 180 | 180 | 0.1 | 180 | 1/2" matte | 22 | 55 | Water | 180 | 0.5 | 52.31 | 0.25 | 13.07 | 3 Row hot water coil
5-3R-80L | 1 | VCWF (Hot Water Heating) | 5" (127mm) | 280 | 280 | 0.24 | 280 | 1/2" matte | 22 | 55 | Water | 180 | 0.5 | 62.18 | 0.25 | 15.54 | 3 Row hot water coil
6-3R-80L | 1 | VCWF (Hot Water Heating) | 6" (152mm) | 400 | 400 | 0.45 | 400 | 1/2" matte | 22 | 55 | Water | 180 | 1 | 46.29 | 0.84 | 23.15 | 3 Row hot water coil
8-3R-80L | 1 | VCWF (Hot Water Heating) | 8" (203mm) | 720 | 720 | 0.67 | 720 | 1/2" matte | 24 | 55 | Water | 180 | 2.5 | 31.07 | 0.53 | 38.87 | 3 Row hot water coil
10-3R-80L | 1 | VCWF (Hot Water Heating) | 10" (254mm) | 1120 | 1120 | 0.68 | 1120 | 1/2" matte | 32 | 55 | Water | 180 | 2.5 | 46.22 | 1.33 | 57.77 | 3 Row hot water coil
12-3R-80L | 1 | VCWF (Hot Water Heating) | 12" (305mm) | 1600 | 1600 | 0.69 | 1600 | 1/2" matte | 41 | 55 | Water | 180 | 3.5 | 43.72 | 0.84 | 76.53 | 3 Row hot water coil
14-3R-80L | 1 | VCWF (Hot Water Heating) | 14" (356mm) | 2400 | 2400 | 0.74 | 2400 | 1/2" matte | 51 | 55 | Water | 180 | 5 | 47.29 | 1.25 | 118.23 | 3 Row hot water coil
16-3R-80L | 1 | VCWF (Hot Water Heating) | 16" (406mm) | 3200 | 3200 | 0.88 | 3200 | 1/2" matte | 56 | 55 | Water | 180 | 5 | 56.6 | 1.34 | 141.43 | 3 Row hot water coil
24-3R-80L | 1 | VCWF (Hot Water Heating) | 24" x 16" (610x406mm) | 5000 | 5000 | 1.95 | 5000 | 1/2" matte | 82 | 55 | Water | 180 | 5 | 79.5 | 1.73 | 198.5 | 4 Row hot water coil
4-3R-80R | 1 | VCWF (Hot Water Heating) | 4" (102mm) | 180 | 180 | 0.1 | 180 | 1/2" matte | 22 | 55 | Water | 180 | 2.5 | 13.87 | 4.22 | 17.37 | 3 Row hot water coil
5-3R-80R | 1 | VCWF (Hot Water Heating) | 5" (127mm) | 280 | 280 | 0.24 | 280 | 1/2" matte | 22 | 55 | Water | 180 | 2.5 | 18.47 | 4.23 | 23.12 | 3 Row hot water coil
6-3R-80R | 1 | VCWF (Hot Water Heating) | 6" (152mm) | 400 | 400 | 0.45 | 400 | 1/2" matte | 22 | 55 | Water | 180 | 2.5 | 22.53 | 4.25 | 28.19 | 3 Row hot water coil
8-3R-80R | 1 | VCWF (Hot Water Heating) | 8" (203mm) | 720 | 720 | 0.67 | 720 | 1/2" matte | 24 | 55 | Water | 180 | 12 | 8.16 | 9.48 | 49.05 | 3 Row hot water coil
10-3R-80R | 1 | VCWF (Hot Water Heating) | 10" (254mm) | 1120 | 1120 | 0.68 | 1120 | 1/2" matte | 32 | 55 | Water | 180 | 10 | 14.85 | 17.15 | 74.35 | 3 Row hot water coil
12-3R-80R | 1 | VCWF (Hot Water Heating) | 12" (305mm) | 1600 | 1600 | 0.69 | 1600 | 1/2" matte | 41 | 55 | Water | 180 | 14 | 14.32 | 11.08 | 100.4 | 3 Row hot water coil
14-3R-80R | 1 | VCWF (Hot Water Heating) | 14" (356mm) | 2400 | 2400 | 0.74 | 2400 | 1/2" matte | 51 | 55 | Water | 180 | 15 | 20.01 | 9.86 | 150.28 | 3 Row hot water coil
16-3R-80R | 1 | VCWF (Hot Water Heating) | 16" (406mm) | 3200 | 3200 | 0.88 | 3200 | 1/2" matte | 56 | 55 | Water | 180 | 17 | 22.43 | 13.25 | 190.86 | 3 Row hot water coil
24-3R-80R | 1 | VCWF (Hot Water Heating) | 24" x 16" (610x406mm) | 5000 | 5000 | 1.46 | 5000 | 1/2" matte | 76 | 55 | Water | 180 | 17 | 29.24 | 14.01 | 248.74 | 3 Row hot water coil
4-4R-80L | 1 | VCWF (Hot Water Heating) | 4" (102mm) | 180 | 180 | 0.14 | 180 | 1/2" matte | 24 | 55 | Water | 180 | 0.5 | 59.94 | 0.33 | 14.98 | 4 Row hot water coil
5-4R-80L | 1 | VCWF (Hot Water Heating) | 5" (127mm) | 280 | 280 | 0.32 | 280 | 1/2" matte | 24 | 55 | Water | 180 | 0.5 | 71.69 | 0.33 | 17.9 | 4 Row hot water coil
6-4R-80L | 1 | VCWF (Hot Water Heating) | 6" (152mm) | 400 | 400 | 0.59 | 400 | 1/2" matte | 24 | 55 | Water | 180 | 1 | 54.38 | 1.11 | 27.18 | 4 Row hot water coil
8-4R-80L | 1 | VCWF (Hot Water Heating) | 8" (203mm) | 720 | 720 | 0.88 | 720 | 1/2" matte | 26 | 55 | Water | 180 | 2.5 | 37.27 | 0.67 | 46.61 | 4 Row hot water coil
10-4R-80L | 1 | VCWF (Hot Water Heating) | 10" (254mm) | 1120 | 1120 | 0.9 | 1120 | 1/2" matte | 36 | 55 | Water | 180 | 2.5 | 54.67 | 1.79 | 68.32 | 4 Row hot water coil
12-4R-80L | 1 | VCWF (Hot Water Heating) | 12" (305mm) | 1600 | 1600 | 0.91 | 1600 | 1/2" matte | 45 | 55 | Water | 180 | 3.5 | 54.16 | 1.02 | 94.76 | 4 Row hot water coil
14-4R-80L | 1 | VCWF (Hot Water Heating) | 14" (356mm) | 2400 | 2400 | 0.96 | 2400 | 1/2" matte | 55 | 55 | Water | 180 | 5 | 56 | 1.48 | 139.95 | 4 Row hot water coil
16-4R-80L | 1 | VCWF (Hot Water Heating) | 16" (406mm) | 3200 | 3200 | 1.17 | 3200 | 1/2" matte | 61 | 55 | Water | 180 | 5 | 66.52 | 1.6 | 166.16 | 4 Row hot water coil
24-4R-80L | 1 | VCWF (Hot Water Heating) | 24" x 16" (610x406mm) | 5000 | 5000 | 1.46 | 5000 | 1/2" matte | 76 | 55 | Water | 180 | 5 | 68.34 | 1.44 | 170.71 | 3 Row hot water coil
4-4R-80R | 1 | VCWF (Hot Water Heating) | 4" (102mm) | 180 | 180 | 0.14 | 180 | 1/2" matte | 24 | 55 | Water | 180 | 2.5 | 15.69 | 5.5 | 19.65 | 4 Row hot water coil
5-4R-80R | 1 | VCWF (Hot Water Heating) | 5" (127mm) | 280 | 280 | 0.32 | 280 | 1/2" matte | 24 | 55 | Water | 180 | 2.5 | 21.44 | 5.52 | 26.83 | 4 Row hot water coil
6-4R-80R | 1 | VCWF (Hot Water Heating) | 6" (152mm) | 400 | 400 | 0.59 | 400 | 1/2" matte | 24 | 55 | Water | 180 | 2.5 | 26.61 | 5.54 | 33.3 | 4 Row hot water coil
8-4R-80R | 1 | VCWF (Hot Water Heating) | 8" (203mm) | 720 | 720 | 0.88 | 720 | 1/2" matte | 26 | 55 | Water | 180 | 12 | 9.78 | 11.6 | 58.8 | 4 Row hot water coil
10-4R-80R | 1 | VCWF (Hot Water Heating) | 10" (254mm) | 1120 | 1120 | 0.9 | 1120 | 1/2" matte | 36 | 55 | Water | 180 | 10 | 17.76 | 22.33 | 88.94 | 4 Row hot water coil
12-4R-80R | 1 | VCWF (Hot Water Heating) | 12" (305mm) | 1600 | 1600 | 0.91 | 1600 | 1/2" matte | 45 | 55 | Water | 180 | 14 | 17.97 | 13.03 | 125.97 | 4 Row hot water coil
14-4R-80R | 1 | VCWF (Hot Water Heating) | 14" (356mm) | 2400 | 2400 | 0.96 | 2400 | 1/2" matte | 55 | 55 | Water | 180 | 15 | 23.98 | 11.37 | 180.07 | 4 Row hot water coil
16-4R-80R | 1 | VCWF (Hot Water Heating) | 16" (406mm) | 3200 | 3200 | 1.17 | 3200 | 1/2" matte | 61 | 55 | Water | 180 | 17 | 26.94 | 15.39 | 229.23 | 4 Row hot water coil
24-4R-80R | 1 | VCWF (Hot Water Heating) | 24" x 16" (610x406mm) | 5000 | 5000 | 1.95 | 5000 | 1/2" matte | 82 | 55 | Water | 180 | 17 | 35.36 | 16.42 | 300.76 | 4 Row hot water coil
4-VCCF-L | 1 | VCCF (Cooling Only) | 4" (102mm) | 112 | 112 | 0.01 | 112 | 1" matte | 16 | 55 | [7 empty] | 69 | 65 | 52 | 50 | 46 | 44 | 26 | 48 | 46 | 42 | 35 | 32 | 25 | 15 | 0.75 | AHRI 885-98/08 | AHRI 885-98/08 Mineral Fiber
5-VCCF-L | 1 | VCCF (Cooling Only) | 5" (127mm) | 175 | 175 | 0.01 | 175 | 1" matte | 16 | 55 | [7 empty] | 63 | 61 | 51 | 49 | 46 | 44 | 20 | 48 | 45 | 40 | 34 | 28 | 24 | 15 | 0.75 | AHRI 885-98/08 | AHRI 885-98/08 Mineral Fiber
6-VCCF-L | 1 | VCCF (Cooling Only) | 6" (152mm) | 250 | 250 | 0.06 | 250 | 1" matte | 16 | 55 | [7 empty] | 63 | 61 | 51 | 49 | 46 | 44 | 19 | 52 | 48 | 42 | 34 | 28 | 24 | 15 | 0.75 | AHRI 885-98/08 | AHRI 885-98/08 Mineral Fiber
8-VCCF-L | 1 | VCCF (Cooling Only) | 8" (203mm) | 450 | 450 | 0.03 | 450 | 1" matte | 16 | 55 | [7 empty] | 63 | 61 | 53 | 49 | 48 | 48 | 19 | 49 | 45 | 43 | 36 | 32 | 26 | 16 | 0.75 | AHRI 885-98/08 | AHRI 885-98/08 Mineral Fiber
10-VCCF-L | 1 | VCCF (Cooling Only) | 10" (254mm) | 700 | 700 | 0.01 | 700 | 1" matte | 22 | 55 | [7 empty] | 63 | 59 | 57 | 55 | 50 | 46 | 15 | 53 | 48 | 46 | 37 | 29 | 26 | 20 | 0.75 | AHRI 885-98/08 | AHRI 885-98/08 Mineral Fiber
12-VCCF-L | 1 | VCCF (Cooling Only) | 12" (305mm) | 1000 | 1000 | 0.01 | 1000 | 1" matte | 27 | 55 | [7 empty] | 62 | 59 | 56 | 53 | 52 | 48 | 15 | 53 | 50 | 44 | 37 | 31 | 28 | 17 | 0.75 | AHRI 885-98/08 | AHRI 885-98/08 Mineral Fiber
14-VCCF-L | 1 | VCCF (Cooling Only) | 14" (356mm) | 1500 | 1500 | 0.01 | 1500 | 1" matte | 32 | 55 | [7 empty] | 63 | 59 | 57 | 52 | 50 | 46 | 15 | 53 | 51 | 41 | 35 | 28 | 25 | 19 | 0.75 | AHRI 885-98/08 | AHRI 885-98/08 Mineral Fiber
16-VCCF-L | 1 | VCCF (Cooling Only) | 16" (406mm) | 2000 | 2000 | 0.01 | 2000 | 1" matte | 35 | 55 | [7 empty] | 63 | 59 | 57 | 54 | 52 | 47 | 15 | 53 | 51 | 44 | 38 | 32 | 27 | 19 | 0.75 | AHRI 885-98/08 | AHRI 885-98/08 Mineral Fiber
24-VCCF-L | 1 | VCCF (Cooling Only) | 24" x 16" (610x406mm) | 4000 | 4000 | 0.08 | 4000 | 1" matte | 52 | 55 | [7 empty] | 75 | 74 | 68 | 65 | 62 | 58 | 34 | 69 | 69 | 60 | 52 | 44 | 36 | 40 | 0.75 | AHRI 885-98/08 | AHRI 885-98/08 Mineral Fiber
4-VCCF-H | 1 | VCCF (Cooling Only) | 4" (102mm) | 180 | 180 | 0.01 | 180 | 1" matte | 16 | 55 | [7 empty] | 72 | 69 | 54 | 54 | 50 | 48 | 30 | 51 | 49 | 45 | 39 | 34 | 28 | 19 | 0.75 | AHRI 885-98/08 | AHRI 885-98/08 Mineral Fiber
5-VCCF-H | 1 | VCCF (Cooling Only) | 5" (127mm) | 280 | 280 | 0.01 | 280 | 1" matte | 16 | 55 | [7 empty] | 68 | 64 | 54 | 53 | 49 | 47 | 25 | 50 | 47 | 43 | 37 | 31 | 26 | 16 | 0.75 | AHRI 885-98/08 | AHRI 885-98/08 Mineral Fiber
6-VCCF-H | 1 | VCCF (Cooling Only) | 6" (152mm) | 400 | 400 | 0.14 | 400 | 1" matte | 16 | 55 | [7 empty] | 68 | 63 | 54 | 52 | 48 | 46 | 21 | 56 | 51 | 46 | 38 | 30 | 26 | 20 | 0.75 | AHRI 885-98/08 | AHRI 885-98/08 Mineral Fiber
8-VCCF-H | 1 | VCCF (Cooling Only) | 8" (203mm) | 720 | 720 | 0.05 | 720 | 1" matte | 16 | 55 | [7 empty] | 67 | 63 | 57 | 54 | 51 | 51 | 21 | 53 | 49 | 47 | 40 | 36 | 30 | 21 | 0.75 | AHRI 885-98/08 | AHRI 885-98/08 Mineral Fiber
10-VCCF-H | 1 | VCCF (Cooling Only) | 10" (254mm) | 1120 | 1120 | 0.01 | 1120 | 1" matte | 22 | 55 | [7 empty] | 69 | 63 | 61 | 58 | 53 | 50 | 20 | 60 | 53 | 49 | 41 | 33 | 28 | 23 | 0.75 | AHRI 885-98/08 | AHRI 885-98/08 Mineral Fiber
12-VCCF-H | 1 | VCCF (Cooling Only) | 12" (305mm) | 1600 | 1600 | 0.01 | 1600 | 1" matte | 27 | 55 | [7 empty] | 66 | 62 | 60 | 56 | 54 | 50 | 19 | 60 | 54 | 48 | 40 | 34 | 30 | 22 | 0.75 | AHRI 885-98/08 | AHRI 885-98/08 Mineral Fiber
14-VCCF-H | 1 | VCCF (Cooling Only) | 14" (356mm) | 2400 | 2400 | 0.01 | 2400 | 1" matte | 32 | 55 | [7 empty] | 68 | 65 | 63 | 56 | 53 | 50 | 22 | 59 | 57 | 48 | 39 | 31 | 28 | 26 | 0.75 | AHRI 885-98/08 | AHRI 885-98/08 Mineral Fiber
16-VCCF-H | 1 | VCCF (Cooling Only) | 16" (406mm) | 3200 | 3200 | 0.01 | 3200 | 1" matte | 35 | 55 | [7 empty] | 68 | 66 | 65 | 59 | 56 | 53 | 24 | 59 | 58 | 51 | 42 | 36 | 31 | 27 | 0.75 | AHRI 885-98/08 | AHRI 885-98/08 Mineral Fiber
24-VCCF-H | 1 | VCCF (Cooling Only) | 24" x 16" (610x406mm) | 6400 | 6400 | 0.23 | 6400 | 1" matte | 52 | 55 | [7 empty] | 75 | 74 | 72 | 69 | 65 | 63 | 34 | 71 | 70 | 65 | 55 | 48 | 41 | 41 | 0.75 | AHRI 885-98/08 | AHRI 885-98/08 Mineral Fiber